## DataFormat
Data_Format | Operation | Product_ID | Sheet_Name
8 Bit Unsigned Integer | 03 Read Holding Registers (4x) | 9 | TSTAT8
8 Bit Signed Integer | 06 Write Single Register | 35 | T3BB
16 Bit Unsigned Integer | 16 Write Multiple Registers | 74 | T3BB
16 Bit Signed Integer | 03_06 Read Holding and Write Single | 216 | CO2_Node
32 Bit Unsigned Integer HI_LO | 03_16 Read Holding and Write Multiple | 44 | T38I8O6DO
32 Bit Unsigned Integer LO_HI | 01 Read Coils (0x) | 43 | T322AI
32 Bit Signed Integer HI_LO | 02 Read Discrete Inputs (1x) | 46 | T3PT12
32 Bit Signed Integer LO_HI | 04 Read Input Registers (3x) | 121 | BTU Meter
Floating HI_LO/10 | 05 Write Single Coil | 95 | T36CTA
Floating LO_HI/10 | 15 Write Multiple Coil | 52 | PM2_5
Floating HI_LO/100 |  | 50 | T3BB
Floating LO_HI/100 |  | 63 | ZIGBEE_REPEATER
Floating HI_LO/1000 |  | 51 | PM5E_ARM
Floating LO_HI/1000 |  | 60 | AirLab
Character String HI_LO |  | 62 | AirLab
Character String LO_HI |  | 10 | T3BB
16 Bit Signed Integer/10 |  | 90 | Transducer2
16 Bit Unsigned Integer/10 |  | 210 | CO2
16 Bit Signed Integer/100 |  | 211 | CO2
16 Bit Unsigned Integer/100 |  | 212 | HUM
32 Bit Float_ABCD |  | 213 | HUM
32 Bit Float_CDAB |  | 96 | AFS
32 Bit Float_BADC |  | 97 | FAN_MODULE
32 Bit Float_DCBA |  | 36 | CS
|  | 37 | CS
|  | 20 | T3_8AI13O
|  | 22 | T3_32I
|  | 88 | T3_XB_ESP
|  | 7 | TSTAT8
|  | 93 | TSTAT8
|  | 214 | Pressure
|  | 215 | Pressure
|  | 36 | SPM1
|  | 37 | SPM1
|  | 53 | T3_32AI_ARM
|  | 250 | MEx37

## T3_32AI_ARM
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
11 | 1 | MODBUS_ISP_VERSION | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | bootloader revision
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | baudrate 0=9600,1=19200,2=38400,3=57600,4=115200,5=76800
21 | 1 | MODBUS_PROTOCOL_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | protocal type. 0=mstp, 3=modbus
22 | 2 | MODBUS_INSTANCE_HIGH | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | high word of instance
23 | 2 | MODBUS_INSTANCE_LOW | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | low word of instance
30 | 1 | MODBUS_OUTPUT_DEAD_MASTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | dead master of outputs
37 | 1 | MODBUS_MAX_MASTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
38 | 1 | MODBUS_BACNET_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
39 | 1 | MODBUS_STATION_NUM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
40 | 6 | MODBUS_MAC | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC address
46 | 1 | MODBUS_IP_MODE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | IP mode. 0=static IP; 1= DHCP
47 | 1 | MODBUS_IP_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
48 | 1 | MODBUS_IP_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
49 | 1 | MODBUS_IP_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
50 | 1 | MODBUS_IP_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
51 | 1 | MODBUS_SUBNET_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
52 | 1 | MODBUS_SUBNET_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
53 | 1 | MODBUS_SUBNET_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
54 | 1 | MODBUS_SUBNET_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
55 | 1 | MODBUS_GETWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
56 | 1 | MODBUS_GETWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
57 | 1 | MODBUS_GETWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
58 | 1 | MODBUS_GETWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
59 | 1 | MODBUS_TCPSERVER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0,TCP server
60 | 1 | MODBUS_TCP_LISTEN_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | listen port at TCP server mode
61 | 1 | MODBUS_GHOST_IP_MODE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Ghost IP mode. 0=static IP; 1= DHCP
62 | 1 | MODBUS_GHOST_IP_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
63 | 1 | MODBUS_GHOST_IP_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
64 | 1 | MODBUS_GHOST_IP_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
65 | 1 | MODBUS_GHOST_IP_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
66 | 1 | MODBUS_GHOST_SUBNET_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
67 | 1 | MODBUS_GHOST_SUBNET_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
68 | 1 | MODBUS_GHOST_SUBNET_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
69 | 1 | MODBUS_GHOST_SUBNET_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
70 | 1 | MODBUS_GHOST_GETWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
71 | 1 | MODBUS_GHOST_GETWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
72 | 1 | MODBUS_GHOST_GETWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
73 | 1 | MODBUS_GHOST_GETWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
74 | 1 | MODBUS_GHOST_TCPSERVER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0,TCP server
75 | 1 | MODBUS_GHOST_TCP_LISTEN_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | listen port at TCP server mode
76 | 1 | MODBUS_WRITE_GHOST_SYSTEM | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
80 | 1 | MODBUS_REPOWER_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | output resume to OFF or last status
90 | 1 | MODBUS_BACNET_VENDOR_ID | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
93 | 1 | MODBUS_MAC_ENABLE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
99 | 1 | MODBUS_SERINALNUMBER_WRITE_FLAG | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
100 | 2 | MODBUS_AI_CHANNLE0_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 0 high byte
101 | 2 | MODBUS_AI_CHANNLE0_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 0 low byte
102 | 2 | MODBUS_AI_CHANNLE1_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 1 high byte
103 | 2 | MODBUS_AI_CHANNLE1_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 1 low byte
104 | 2 | MODBUS_AI_CHANNLE2_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 2 high byte
105 | 2 | MODBUS_AI_CHANNLE2_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 2 low byte
106 | 2 | MODBUS_AI_CHANNLE3_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 3 high byte
107 | 2 | MODBUS_AI_CHANNLE3_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 3 low byte
108 | 2 | MODBUS_AI_CHANNLE4_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 4 high byte
109 | 2 | MODBUS_AI_CHANNLE4_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 4 low byte
110 | 2 | MODBUS_AI_CHANNLE5_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 5 high byte
111 | 2 | MODBUS_AI_CHANNLE5_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 5 low byte
112 | 2 | MODBUS_AI_CHANNLE6_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 6 high byte
113 | 2 | MODBUS_AI_CHANNLE6_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 6 low byte
114 | 2 | MODBUS_AI_CHANNLE7_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 7 high byte
115 | 2 | MODBUS_AI_CHANNLE7_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 7 low byte
116 | 2 | MODBUS_AI_CHANNLE8_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 8 high byte
117 | 2 | MODBUS_AI_CHANNLE8_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 8 low byte
118 | 2 | MODBUS_AI_CHANNLE9_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 9 high byte
119 | 2 | MODBUS_AI_CHANNLE9_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 9 low byte
120 | 2 | MODBUS_AI_CHANNLE10_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 10 high byte
121 | 2 | MODBUS_AI_CHANNLE10_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 10 low byte
122 | 2 | MODBUS_AI_CHANNLE11_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 11 high byte
123 | 2 | MODBUS_AI_CHANNLE11_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 11 low byte
124 | 2 | MODBUS_AI_CHANNLE12_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 12 high byte
125 | 2 | MODBUS_AI_CHANNLE12_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 12 low byte
126 | 2 | MODBUS_AI_CHANNLE13_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 13 high byte
127 | 2 | MODBUS_AI_CHANNLE13_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 13 low byte
128 | 2 | MODBUS_AI_CHANNLE14_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 14 high byte
129 | 2 | MODBUS_AI_CHANNLE14_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 14 low byte
130 | 2 | MODBUS_AI_CHANNLE15_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 15 high byte
131 | 2 | MODBUS_AI_CHANNLE15_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 15 low byte
132 | 2 | MODBUS_AI_CHANNLE16_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 16 high byte
133 | 2 | MODBUS_AI_CHANNLE16_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 16 low byte
134 | 2 | MODBUS_AI_CHANNLE17_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 17 high byte
135 | 2 | MODBUS_AI_CHANNLE17_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 17 low byte
136 | 2 | MODBUS_AI_CHANNLE18_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 18 high byte
137 | 2 | MODBUS_AI_CHANNLE18_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 18 low byte
138 | 2 | MODBUS_AI_CHANNLE19_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 19 high byte
139 | 2 | MODBUS_AI_CHANNLE19_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 19 low byte
140 | 2 | MODBUS_AI_CHANNLE20_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 20 high byte
141 | 2 | MODBUS_AI_CHANNLE20_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 20 low byte
142 | 2 | MODBUS_AI_CHANNLE21_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 21 high byte
143 | 2 | MODBUS_AI_CHANNLE21_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 21 low byte
144 | 2 | MODBUS_AI_CHANNLE22_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 22 high byte
145 | 2 | MODBUS_AI_CHANNLE22_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 22 low byte
146 | 2 | MODBUS_AI_CHANNLE23_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 23 high byte
147 | 2 | MODBUS_AI_CHANNLE23_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 23 low byte
148 | 2 | MODBUS_AI_CHANNLE24_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 24 high byte
149 | 2 | MODBUS_AI_CHANNLE24_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 24 low byte
150 | 2 | MODBUS_AI_CHANNLE25_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 25 high byte
151 | 2 | MODBUS_AI_CHANNLE25_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 25 low byte
152 | 2 | MODBUS_AI_CHANNLE26_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 26 high byte
153 | 2 | MODBUS_AI_CHANNLE26_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 26 low byte
154 | 2 | MODBUS_AI_CHANNLE27_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 27 high byte
155 | 2 | MODBUS_AI_CHANNLE27_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 27 low byte
156 | 2 | MODBUS_AI_CHANNLE28_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 28 high byte
157 | 2 | MODBUS_AI_CHANNLE28_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 28 low byte
158 | 2 | MODBUS_AI_CHANNLE29_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 29 high byte
159 | 2 | MODBUS_AI_CHANNLE29_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 29 low byte
160 | 2 | MODBUS_AI_CHANNLE30_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 30 high byte
161 | 2 | MODBUS_AI_CHANNLE30_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 30 low byte
162 | 2 | MODBUS_AI_CHANNLE31_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 31 high byte
163 | 2 | MODBUS_AI_CHANNLE31_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 31 low byte
164 | 1 | MODBUS_AI_FILTER0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 0 filter
165 | 1 | MODBUS_AI_FILTER1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 1 filter
166 | 1 | MODBUS_AI_FILTER2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 2 filter
167 | 1 | MODBUS_AI_FILTER3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 3 filter
168 | 1 | MODBUS_AI_FILTER4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 4 filter
169 | 1 | MODBUS_AI_FILTER5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 5 filter
170 | 1 | MODBUS_AI_FILTER6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 6 filter
171 | 1 | MODBUS_AI_FILTER7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 7 filter
172 | 1 | MODBUS_AI_FILTER8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 8 filter
173 | 1 | MODBUS_AI_FILTER9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 9 filter
174 | 1 | MODBUS_AI_FILTER10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 10 filter
175 | 1 | MODBUS_AI_FILTER11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 11 filter
176 | 1 | MODBUS_AI_FILTER12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 12 filter
177 | 1 | MODBUS_AI_FILTER13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 13 filter
178 | 1 | MODBUS_AI_FILTER14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 14 filter
179 | 1 | MODBUS_AI_FILTER15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 15 filter
180 | 1 | MODBUS_AI_FILTER16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 16 filter
181 | 1 | MODBUS_AI_FILTER17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 17 filter
182 | 1 | MODBUS_AI_FILTER18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 18 filter
183 | 1 | MODBUS_AI_FILTER19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 19 filter
184 | 1 | MODBUS_AI_FILTER20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 20 filter
185 | 1 | MODBUS_AI_FILTER21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 21 filter
186 | 1 | MODBUS_AI_FILTER22 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 22 filter
187 | 1 | MODBUS_AI_FILTER23 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 23 filter
188 | 1 | MODBUS_AI_FILTER24 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 24 filter
189 | 1 | MODBUS_AI_FILTER25 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 25 filter
190 | 1 | MODBUS_AI_FILTER26 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 26 filter
191 | 1 | MODBUS_AI_FILTER27 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 27 filter
192 | 1 | MODBUS_AI_FILTER28 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 28 filter
193 | 1 | MODBUS_AI_FILTER29 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 29 filter
194 | 1 | MODBUS_AI_FILTER30 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 30 filter
195 | 1 | MODBUS_AI_FILTER31 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 31 filter
196 | 1 | MODBUS_AI_RANGE0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 0 range. if analog inputs (not_used_input = 0, Y3K_40_150DegC, Y3K_40_300DegF, R10K_40_120DegC, R10K_40_250DegF, R3K_40_150DegC, R3K_40_300DegF, KM10K_40_120DegC, KM10K_40_250DegF, A10K_50_110DegC, A10K_60_200DegF, V0_5, I0_100Amps, I0_20ma, I0_20psi, N0_2_32counts, N0_3000FPM_0_5V, P0_100_0_5V, P0_100_4_20ma, P0_255p_min, table1, table2, table3, table4, table5,100 - HI_SPEED_COUNTER ), if digital inputs(not_used_input = 0,OFF_ON, CLOSED_OPEN, STOP_START, DISABLED_ENABLED, NORMAL_ALARM, NORMAL_HIGH, NORMAL_LOW, NO_YES, COOL_HEAT, UNOCCUPIED_OCCUPIED, LOW_HIGH, ON_OFF , OPEN_CLOSED, START_STOP, ENABLED_DISABLED, ALARM_NORMAL, HIGH_NORMAL, LOW_NORMAL, YES_NO, HEAT_COOL, OCCUPIED_UNOCCUPIED, HIGH_LOW, custom_digital1, custom_digital2, custom_digital3, custom_digital4, custom_digital5, custom_digital6, custom_digital7, custom_digital8 )
197 | 1 | MODBUS_AI_RANGE1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 1 range
198 | 1 | MODBUS_AI_RANGE2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 2 range
199 | 1 | MODBUS_AI_RANGE3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 3 range
200 | 1 | MODBUS_AI_RANGE4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 4 range
201 | 1 | MODBUS_AI_RANGE5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 5 range
202 | 1 | MODBUS_AI_RANGE6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 6 range
203 | 1 | MODBUS_AI_RANGE7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 7 range
204 | 1 | MODBUS_AI_RANGE8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 8 range
205 | 1 | MODBUS_AI_RANGE9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 9 range
206 | 1 | MODBUS_AI_RANGE10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 10 range
207 | 1 | MODBUS_AI_RANGE11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 11 range
208 | 1 | MODBUS_AI_RANGE12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 12 range
209 | 1 | MODBUS_AI_RANGE13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 13 range
210 | 1 | MODBUS_AI_RANGE14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 14 range
211 | 1 | MODBUS_AI_RANGE15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 15 range
212 | 1 | MODBUS_AI_RANGE16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 16 range
213 | 1 | MODBUS_AI_RANGE17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 17 range
214 | 1 | MODBUS_AI_RANGE18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 18 range
215 | 1 | MODBUS_AI_RANGE19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 19 range
216 | 1 | MODBUS_AI_RANGE20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 20 range
217 | 1 | MODBUS_AI_RANGE21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 21 range
218 | 1 | MODBUS_AI_RANGE22 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 22 range
219 | 1 | MODBUS_AI_RANGE23 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 23 range
220 | 1 | MODBUS_AI_RANGE24 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 24 range
221 | 1 | MODBUS_AI_RANGE25 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 25 range
222 | 1 | MODBUS_AI_RANGE26 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 26 range
223 | 1 | MODBUS_AI_RANGE27 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 27 range
224 | 1 | MODBUS_AI_RANGE28 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 28 range
225 | 1 | MODBUS_AI_RANGE29 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 29 range
226 | 1 | MODBUS_AI_RANGE30 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 30 range
227 | 1 | MODBUS_AI_RANGE31 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 31 range
228 | 1 | MODBUS_AUTO_MANUAL_0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 0
229 | 1 | MODBUS_AUTO_MANUAL_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 1
230 | 1 | MODBUS_AUTO_MANUAL_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 2
231 | 1 | MODBUS_AUTO_MANUAL_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 3
232 | 1 | MODBUS_AUTO_MANUAL_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 4
233 | 1 | MODBUS_AUTO_MANUAL_5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 5
234 | 1 | MODBUS_AUTO_MANUAL_6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 6
235 | 1 | MODBUS_AUTO_MANUAL_7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 7
236 | 1 | MODBUS_AUTO_MANUAL_8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 8
237 | 1 | MODBUS_AUTO_MANUAL_9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 9
238 | 1 | MODBUS_AUTO_MANUAL_10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 10
239 | 1 | MODBUS_AUTO_MANUAL_11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 11
240 | 1 | MODBUS_AUTO_MANUAL_12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 12
241 | 1 | MODBUS_AUTO_MANUAL_13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 13
242 | 1 | MODBUS_AUTO_MANUAL_14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 14
243 | 1 | MODBUS_AUTO_MANUAL_15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 15
244 | 1 | MODBUS_AUTO_MANUAL_16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 16
245 | 1 | MODBUS_AUTO_MANUAL_17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 17
246 | 1 | MODBUS_AUTO_MANUAL_18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 18
247 | 1 | MODBUS_AUTO_MANUAL_19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 19
248 | 1 | MODBUS_AUTO_MANUAL_20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 20
249 | 1 | MODBUS_AUTO_MANUAL_21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 21
250 | 1 | MODBUS_AUTO_MANUAL_22 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 22
251 | 1 | MODBUS_AUTO_MANUAL_23 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 23
252 | 1 | MODBUS_AUTO_MANUAL_24 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 24
253 | 1 | MODBUS_AUTO_MANUAL_25 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 25
254 | 1 | MODBUS_AUTO_MANUAL_26 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 26
255 | 1 | MODBUS_AUTO_MANUAL_27 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 27
256 | 1 | MODBUS_AUTO_MANUAL_28 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 28
257 | 1 | MODBUS_AUTO_MANUAL_29 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 29
258 | 1 | MODBUS_AUTO_MANUAL_30 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 30
259 | 1 | MODBUS_AUTO_MANUAL_31 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 31
260 | 1 | MODBUS_AI_DI_AI0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input0 ( 0 - digital 1 - analog)
261 | 1 | MODBUS_AI_DI_AI1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input1
262 | 1 | MODBUS_AI_DI_AI2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input2
263 | 1 | MODBUS_AI_DI_AI3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input3
264 | 1 | MODBUS_AI_DI_AI4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input4
265 | 1 | MODBUS_AI_DI_AI5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input5
266 | 1 | MODBUS_AI_DI_AI6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input6
267 | 1 | MODBUS_AI_DI_AI7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input7
268 | 1 | MODBUS_AI_DI_AI8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input8
269 | 1 | MODBUS_AI_DI_AI9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input9
270 | 1 | MODBUS_AI_DI_AI10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input10
271 | 1 | MODBUS_AI_DI_AI11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input11
272 | 1 | MODBUS_AI_DI_AI12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input12
273 | 1 | MODBUS_AI_DI_AI13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input13
274 | 1 | MODBUS_AI_DI_AI14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input14
275 | 1 | MODBUS_AI_DI_AI15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input15
276 | 1 | MODBUS_AI_DI_AI16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input16
277 | 1 | MODBUS_AI_DI_AI17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input17
278 | 1 | MODBUS_AI_DI_AI18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input18
279 | 1 | MODBUS_AI_DI_AI19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input19
280 | 1 | MODBUS_AI_DI_AI20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input20
281 | 1 | MODBUS_AI_DI_AI21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input21
282 | 1 | MODBUS_AI_DI_AI22 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input22
283 | 1 | MODBUS_AI_DI_AI23 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input23
284 | 1 | MODBUS_AI_DI_AI24 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input24
285 | 1 | MODBUS_AI_DI_AI25 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input25
286 | 1 | MODBUS_AI_DI_AI26 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input26
287 | 1 | MODBUS_AI_DI_AI27 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input27
288 | 1 | MODBUS_AI_DI_AI28 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input28
289 | 1 | MODBUS_AI_DI_AI29 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input29
290 | 1 | MODBUS_AI_DI_AI30 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input30
291 | 1 | MODBUS_AI_DI_AI31 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input31
292 | 1 | MODBUS_AI_JUPER0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
293 | 1 | MODBUS_AI_JUPER1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
294 | 1 | MODBUS_AI_JUPER2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
295 | 1 | MODBUS_AI_JUPER3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
296 | 1 | MODBUS_AI_JUPER4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
297 | 1 | MODBUS_AI_JUPER5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
298 | 1 | MODBUS_AI_JUPER6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
299 | 1 | MODBUS_AI_JUPER7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
300 | 1 | MODBUS_AI_JUPER8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
301 | 1 | MODBUS_AI_JUPER9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
302 | 1 | MODBUS_AI_JUPER10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
303 | 1 | MODBUS_AI_JUPER11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
304 | 1 | MODBUS_AI_JUPER12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
305 | 1 | MODBUS_AI_JUPER13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
306 | 1 | MODBUS_AI_JUPER14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
307 | 1 | MODBUS_AI_JUPER15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
308 | 1 | MODBUS_AI_JUPER16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
309 | 1 | MODBUS_AI_JUPER17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
310 | 1 | MODBUS_AI_JUPER18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
311 | 1 | MODBUS_AI_JUPER19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
312 | 1 | MODBUS_AI_JUPER20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
313 | 1 | MODBUS_AI_JUPER21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
314 | 1 | MODBUS_AI_JUPER22 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
315 | 1 | MODBUS_AI_JUPER23 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
316 | 1 | MODBUS_AI_JUPER24 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
317 | 1 | MODBUS_AI_JUPER25 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
318 | 1 | MODBUS_AI_JUPER26 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
319 | 1 | MODBUS_AI_JUPER27 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
320 | 1 | MODBUS_AI_JUPER28 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
321 | 1 | MODBUS_AI_JUPER29 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
322 | 1 | MODBUS_AI_JUPER30 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
323 | 1 | MODBUS_AI_JUPER31 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
324 | 1 | MODBUS_CAL_SIGN0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 0
325 | 1 | MODBUS_CAL_SIGN1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 1
326 | 1 | MODBUS_CAL_SIGN2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 2
327 | 1 | MODBUS_CAL_SIGN3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 3
328 | 1 | MODBUS_CAL_SIGN4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 4
329 | 1 | MODBUS_CAL_SIGN5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 5
330 | 1 | MODBUS_CAL_SIGN6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 6
331 | 1 | MODBUS_CAL_SIGN7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 7
332 | 1 | MODBUS_CAL_SIGN8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 8
333 | 1 | MODBUS_CAL_SIGN9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 9
334 | 1 | MODBUS_CAL_SIGN10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 10
335 | 1 | MODBUS_CAL_SIGN11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 11
336 | 1 | MODBUS_CAL_SIGN12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 12
337 | 1 | MODBUS_CAL_SIGN13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 13
338 | 1 | MODBUS_CAL_SIGN14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 14
339 | 1 | MODBUS_CAL_SIGN15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 15
340 | 1 | MODBUS_CAL_SIGN16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 16
341 | 1 | MODBUS_CAL_SIGN17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 17
342 | 1 | MODBUS_CAL_SIGN18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 18
343 | 1 | MODBUS_CAL_SIGN19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 19
344 | 1 | MODBUS_CAL_SIGN20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 20
345 | 1 | MODBUS_CAL_SIGN21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 21
346 | 1 | MODBUS_CAL_SIGN22 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 22
347 | 1 | MODBUS_CAL_SIGN23 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 23
348 | 1 | MODBUS_CAL_SIGN24 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 24
349 | 1 | MODBUS_CAL_SIGN25 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 25
350 | 1 | MODBUS_CAL_SIGN26 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 26
351 | 1 | MODBUS_CAL_SIGN27 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 27
352 | 1 | MODBUS_CAL_SIGN28 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 28
353 | 1 | MODBUS_CAL_SIGN29 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 29
354 | 1 | MODBUS_CAL_SIGN30 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 30
355 | 1 | MODBUS_CAL_SIGN31 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 31
356 | 2 | MODBUS_CAL0_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input0
357 | 2 | MODBUS_CAL0_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input0
358 | 2 | MODBUS_CAL1_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input1
359 | 2 | MODBUS_CAL1_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input1
360 | 2 | MODBUS_CAL2_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input2
361 | 2 | MODBUS_CAL2_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input2
362 | 2 | MODBUS_CAL3_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input3
363 | 2 | MODBUS_CAL3_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input3
364 | 2 | MODBUS_CAL4_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input4
365 | 2 | MODBUS_CAL4_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input4
366 | 2 | MODBUS_CAL5_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input5
367 | 2 | MODBUS_CAL5_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input5
368 | 2 | MODBUS_CAL6_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input6
369 | 2 | MODBUS_CAL6_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input6
370 | 2 | MODBUS_CAL7_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input7
371 | 2 | MODBUS_CAL7_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input7
372 | 2 | MODBUS_CAL8_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input8
373 | 2 | MODBUS_CAL8_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input8
374 | 2 | MODBUS_CAL9_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input9
375 | 2 | MODBUS_CAL9_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input9
376 | 2 | MODBUS_CAL10_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input10
377 | 2 | MODBUS_CAL10_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input10
378 | 2 | MODBUS_CAL11_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input11
379 | 2 | MODBUS_CAL11_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input11
380 | 2 | MODBUS_CAL12_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input12
381 | 2 | MODBUS_CAL12_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input12
382 | 2 | MODBUS_CAL13_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input13
383 | 2 | MODBUS_CAL13_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input13
384 | 2 | MODBUS_CAL14_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input14
385 | 2 | MODBUS_CAL14_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input14
386 | 2 | MODBUS_CAL15_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input15
387 | 2 | MODBUS_CAL15_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input15
388 | 2 | MODBUS_CAL16_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input16
389 | 2 | MODBUS_CAL16_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input16
390 | 2 | MODBUS_CAL17_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input17
391 | 2 | MODBUS_CAL17_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input17
392 | 2 | MODBUS_CAL18_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input18
393 | 2 | MODBUS_CAL18_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input18
394 | 2 | MODBUS_CAL19_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input19
395 | 2 | MODBUS_CAL19_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input19
396 | 2 | MODBUS_CAL20_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input20
397 | 2 | MODBUS_CAL20_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input20
398 | 2 | MODBUS_CAL21_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input21
399 | 2 | MODBUS_CAL21_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input21
400 | 2 | MODBUS_CAL22_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input22
401 | 2 | MODBUS_CAL22_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input22
402 | 2 | MODBUS_CAL23_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input23
403 | 2 | MODBUS_CAL23_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input23
404 | 2 | MODBUS_CAL24_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input24
405 | 2 | MODBUS_CAL24_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input24
406 | 2 | MODBUS_CAL25_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input25
407 | 2 | MODBUS_CAL25_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input25
408 | 2 | MODBUS_CAL26_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input26
409 | 2 | MODBUS_CAL26_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input26
410 | 2 | MODBUS_CAL27_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input27
411 | 2 | MODBUS_CAL27_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input27
412 | 2 | MODBUS_CAL28_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input28
413 | 2 | MODBUS_CAL28_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input28
414 | 2 | MODBUS_CAL29_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input29
415 | 2 | MODBUS_CAL29_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input29
416 | 2 | MODBUS_CAL30_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input30
417 | 2 | MODBUS_CAL30_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input30
418 | 2 | MODBUS_CAL31_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input31
419 | 2 | MODBUS_CAL31_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input31
420 | 1 | MODBUS_AI0_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
421 | 1 | MODBUS_AI1_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
422 | 1 | MODBUS_AI2_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
423 | 1 | MODBUS_AI3_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
424 | 1 | MODBUS_AI4_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
425 | 1 | MODBUS_AI5_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
426 | 1 | MODBUS_AI6_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
427 | 1 | MODBUS_AI7_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
428 | 1 | MODBUS_AI8_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
429 | 1 | MODBUS_AI9_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
430 | 1 | MODBUS_AI10_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
431 | 1 | MODBUS_AI11_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
432 | 1 | MODBUS_AI12_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
433 | 1 | MODBUS_AI13_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
434 | 1 | MODBUS_AI14_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
435 | 1 | MODBUS_AI15_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
436 | 1 | MODBUS_AI16_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
437 | 1 | MODBUS_AI17_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
438 | 1 | MODBUS_AI18_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
439 | 1 | MODBUS_AI19_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
440 | 1 | MODBUS_AI20_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
441 | 1 | MODBUS_AI21_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
442 | 1 | MODBUS_AI22_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
443 | 1 | MODBUS_AI23_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
444 | 1 | MODBUS_AI24_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
445 | 1 | MODBUS_AI25_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
446 | 1 | MODBUS_AI26_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
447 | 1 | MODBUS_AI27_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
448 | 1 | MODBUS_AI28_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
449 | 1 | MODBUS_AI29_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
450 | 1 | MODBUS_AI30_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
451 | 1 | MODBUS_AI31_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
800 | 1 | MODBUS_RESET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 1-> reset to factory, other -> reset

## SPM1
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | Serial Number - 4 byte value. Read-only
4 | 2 | MODBUS_VERSION_NUMBER_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Software Version – 2 byte value. Read-only
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | ADDRESS. Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Product Model. This is a read-only register that is used by the microcontroller to determine the product
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
100 | 1 | MODBUS_CURRENT_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Range:AC:0-50A;DC:0-100A.The current sensor reading, calibrated value;AC:eg.102 is 1.02A(0.01A)DC:eg.102 is 10.2A(0.1A)
101 | 1 | MODBUS_VOLTAGE_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Range:AC:0-260V;DC:0-380V.The voltage sensor reading, calibrated value.eg.1102 is 110.2V(0.1V)
102 | 1 | MODBUS_VOLTAGE_CAL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibration voltage, only for 50A AND 150A DC sensor
103 | 1 | MODBUS_OUTPUT_BUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0:RS485. 1:one wire
104 | 1 | MODBUS_CURRENT_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0-10(old type),12 - 50A, 13 - 150A
121 | 1 | MODBUS_1ST_CALI_VOLT_TARGET_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | when calibrate,need to set R139=11 and R140=22.Range:0~3800
122 | 1 | MODBUS_1ST_CALI_VOLT_ORIGINAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
123 | 1 | MODBUS_2ND_CALI_VOLT_TARGET_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
124 | 1 | MODBUS_2ND_CALI_VOLT_ORIGINAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
125 | 1 | MODBUS_3RD_CALI_VOLT_TARGET_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
126 | 1 | MODBUS_3RD_CALI_VOLT_ORIGINAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
127 | 1 | MODBUS_4TH_CALI_VOLT_TARGET_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
128 | 1 | MODBUS_4TH_CALI_VOLT_ORIGINAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
129 | 1 | MODBUS_5TH_CALI_VOLT_TARGET_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
130 | 1 | MODBUS_5TH_CALI_VOLT_ORIGINAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
131 | 1 | MODBUS_RATE_CALI_0_10A | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Range:0-5000;the rate of calibrate(0-10A)
132 | 1 | MODBUS_RATE_CALI_0_20A | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Range:0-5000;the rate of calibrate(0-20A)
133 | 1 | MODBUS_RATE_CALI_0_50A | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Range:0-5000;the rate of calibrate(0-50A)
134 | 1 | MODBUS_CURRENT_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
135 | 1 | MODBUS_VOLTAGE_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
136 | 1 | MODBUS_CURRENT_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Range:0-10
137 | 1 | MODBUS_VOLATE_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Range:0-10
139 | 1 | MODBUS_LOCK_SET_X | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | when lockx =11 and lock_y=22,we can calibrate sensor
140 | 1 | MODBUS_LOCK_SET_Y | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
141 | 1 | MODBUS_BAUD_RATE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0:19200.1:9600
142 | 1 | MODBUS_OUTPUT_SET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0:current.1:voltage
143 | 1 | MODBUS_OUTMODE_SET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0:auto.1:manual
144 | 1 | MODBUS_MANUAL_INPUT_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
145 | 1 | MODBUS_CURRENT_SET_OUTPUT_RANGE_A | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
146 | 1 | MODBUS_CURRENT_SET_OUTPUT_RANGE_V | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer

## T3BB
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 1 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version Low
5 | 1 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version High
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
9 | 1 | MODBUS_PIC | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIC rev
12 | 1 | MODBUS_UART0_BAUDRATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
14 | 1 | MODBUS_ISP_VER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | ISP Version
18 | 1 | MODBUS_UART1_BAUDRATE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
19 | 1 | MODBUS_UART2_BAUDRATE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | UART2 Baudrate.(UART_1200 = 0, UART_2400 = 1, UART_3600 = 2, UART_4800 = 3, UART_7200 = 4, UART_9600 = 5, UART_19200 = 6, UART_38400 = 7, UART_76800 = 8, UART_115200 = 9, UART_921600 = 10, UART_57600 = 11
32 | 1 | MODBUS_INSTANCE_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | High word of instance number
33 | 1 | MODBUS_RESET | 06 Write Single Register | 16 Bit Unsigned Integer | write 111 to reset
34 | 1 | MODBUS_MINI_TYPE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Board type, big or small. 1 - big , 2 - samll,3-tiny,4-vav
35 | 1 | MODBUS_INSTANCE_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Low word of instance number
36 | 1 | MODBUS_PANEL_NUMBER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Panel number
37 | 1 | MODBUS_BACKLIGHT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Whetehr enalbe backlight,only for T3-BB. 0 - is disable, 1 - enable
38 | 1 | MODBUS_BIP_PORT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | BIP PORT, default is 47808
39 | 1 | MODBUS_EN_TIME_SYNC_PC | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | EN clear tstat db
40 | 1 | MODBUS_LOGIN_USERNAME_PASSWORD | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 not used 1 disable username and passwork 2 enable
42 | 1 | MODBUS_STATION_NUM | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Station NUM of mstp commucnication
43 | 1 | MODBUS_EN_DYNDNS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | EN DYNDNS , 0 - no 1 - disable 2 - enable
44 | 1 | MODBUS_DYNDNS_PROVIDER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | DYNDNS provider, // 0- www.3322.org 1-www.dyndns.com 2 - www.no-ip.com
45 | 1 | MODBUS_DYNDNS_UPDATE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | dyndns update timer
46 | 1 | MODBUS_NETWORK_NUMBER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | NETWORK_NUMBER
47 | 1 | MODBUS_MSTP_NETWORK | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | MSTP NETWORK
59 | 1 | MODBUS_COM0_TYPE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | com0 configure NOUSE = 0, BACNET_SLAVE = 1, MODBUS_SLAVE = 2, MODBUS_MASTER = 7, RS232_METER = 8, BACNET_MASTER = 9,
60 | 1 | MODBUS_COM1_TYPE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | com1 configure NOUSE = 0, BACNET_SLAVE = 1, MODBUS_SLAVE = 2, MODBUS_MASTER = 7, RS232_METER = 8, BACNET_MASTER = 9,
61 | 1 | MODBUS_COM2_TYPE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | com2 configure NOUSE = 0, BACNET_SLAVE = 1, MODBUS_SLAVE = 2, MODBUS_MASTER = 7, RS232_METER = 8, BACNET_MASTER = 9,
62 | 1 | MODBUS_REFRESH_FLASH | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | write flash time after changed setting. Unit is minute
70 | 1 | MODBUS_OUTPUT_1V | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog output 1v setting, default is 70
71 | 1 | MODBUS_OUTPUT_2V | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog output 2v setting, default is 100
72 | 1 | MODBUS_OUTPUT_3V | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog output 3v setting, default is 120
73 | 1 | MODBUS_OUTPUT_4V | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog output 4v setting, default is 160
74 | 1 | MODBUS_OUTPUT_5V | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog output 5v setting, default is 250
75 | 1 | MODBUS_OUTPUT_6V | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog output 6v setting, default is 420
76 | 1 | MODBUS_OUTPUT_7V | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog output 7v setting, default is 610
77 | 1 | MODBUS_OUTPUT_8V | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog output 8v setting, default is 710
78 | 1 | MODBUS_OUTPUT_9V | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog output 9v setting, default is 800
79 | 1 | MODBUS_OUTPUT_10V | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog output 10v setting, default is 1000
91 | 1 | Modbus_Fix_Com_Config | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Whetehr enalbe backlight,only for T3-BB. 0 - is disable, 1 - enable
94 | 2 | MODBUS_RUN_TIME | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | run time,94 is low word, 95 is high word.
98 | 1 | MODBUS_LCD_TIME_OFF_DELAY | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | For TSTAT10, 0 - BACKLIGHT OFF, 255-BACKLIGHT ON, other - delay time
100 | 6 | MODBUS_MAC | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC address
106 | 1 | MODBUS_TCP_TYPE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | IP mode. 0=static IP; 1= DHCP
107 | 1 | MODBUS_IP_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
108 | 1 | MODBUS_IP_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
109 | 1 | MODBUS_IP_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
110 | 1 | MODBUS_IP_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
111 | 1 | MODBUS_SUBNET_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | subnet
112 | 1 | MODBUS_SUBNET_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | subnet
113 | 1 | MODBUS_SUBNET_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | subnet
114 | 1 | MODBUS_SUBNET_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | subnet
115 | 1 | MODBUS_GETWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | getway
116 | 1 | MODBUS_GETWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | getway
117 | 1 | MODBUS_GETWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | getway
118 | 1 | MODBUS_GETWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | getway
119 | 1 | MODBUS_TCPSERVER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0,TCP server
120 | 1 | MODBUS_TCP_LISTEN_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | listen port at TCP server mode
200 | 1 | MODBUS_TIMER_SYNC_SECOND | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:second
201 | 1 | MODBUS_TIMER_SYNC_MIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync: min
202 | 1 | MODBUS_TIMER_SYNC_HOUR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:hour
203 | 1 | MODBUS_TIMER_SYNC_DAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:day
204 | 1 | MODBUS_TIMER_SYNC_DAY_OF_WEEK | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:day of week
205 | 1 | MODBUS_TIMER_SYNC_MONTH | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:month
206 | 1 | MODBUS_TIMER_SYNC_YEAR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:year
299 | 1 | MODBUS_TOTAL_NO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Number of tstat
300 | 1 | MODBUS_SUBADDR_FIRST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | id of sub tstat ,from 300 to 400
729 | 1 | MODBUS_DISALBE_TSTAT10_DIS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | display icons and scrolling string, 0 - default show icon and scrolling string, 1 - disable both , 2 - show scrolling, no icon
730 | 1 | MODBUS_TSTAT10_TEMPERATURE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | temperature of tstat10
731 | 1 | MODBUS_TSTAT10_TVOC | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | tvoc of tstat10
732 | 1 | MODBUS_TSTAT10_HUMIDITY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | humidity of tstat10
733 | 1 | MODBUS_TSTAT10_OCCUPIED | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | occupide status of tstat10
734 | 1 | MODBUS_TSTAT10_CO2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | co2 of tstat10
735 | 1 | MODBUS_TSTAT10_LIGHT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | light of tstat10
736 | 1 | MODBUS_TSTAT10_VOICE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | voice of tstat10
740 | 1 | MODBUS_TSTAT10_PULSE1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | pulse count1 of tstat10
741 | 1 | MODBUS_TSTAT10_PULSE2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | pulse count2 of tstat10
742 | 1 | MODBUS_TSTAT10_PULSE3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | pulse count3 of tstat10
743 | 1 | MODBUS_TSTAT10_PULSE4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | pulse count4 of tstat10
744 | 1 | MODBUS_TSTAT10_CO2_CALIBRATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | calibration value of CO2
745 | 1 | MODBUS_TSTAT10_HUM_DEW_PT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | DEW point of HUM, uint is C
746 | 1 | MODBUS_TSTAT10_HUM_DEW_PT_F | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | DEW point of HUM, uint is F
747 | 1 | MODBUS_TSTAT10_HUM_PWS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | HumSensor_Pws
748 | 1 | MODBUS_TSTAT10_HUM_MIX_RADIO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | HumSensor_Mix_Ratio
749 | 1 | MODBUS_TSTAT10_HUM_ENTHALPY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | HumSensor_Enthalpy
2000 | 1 | MODBUS_WIFI_SSID_MANUAL_EN | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Enable wifi. 0 - default, 1 - Enable, 2 - disable
2001 | 1 | MODBUS_WIFI_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI IP MODE , 0-DHCP,1-STATIC
2004 | 1 | MODBUS_WIFI_MODBUS_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WIFI_MODBUS_PORT ,Default value :502
2005 | 1 | MODBUS_WIFI_BACNET_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | BACnet PORT , Default value :47808
2010 | 32 | MODBUS_WIFI_SSID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | WIFI_SSID
2042 | 16 | MODBUS_WIFI_PASSWORD | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | WIFI_PASSWORD
2058 | 1 | MODBUS_WIFI_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_IP_ADDRESS_1
2059 | 1 | MODBUS_WIFI_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_IP_ADDRESS_2
2060 | 1 | MODBUS_WIFI_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_IP_ADDRESS_3
2061 | 1 | MODBUS_WIFI_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_IP_ADDRESS_4
2062 | 1 | MODBUS_WIFI_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_SUBNET_MASK_1
2063 | 1 | MODBUS_WIFI_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_SUBNET_MASK_2
2064 | 1 | MODBUS_WIFI_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_SUBNET_MASK_3
2065 | 1 | MODBUS_WIFI_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_SUBNET_MASK_4
2066 | 1 | MODBUS_WIFI_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_GATEWAY_1
2067 | 1 | MODBUS_WIFI_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_GATEWAY_2
2068 | 1 | MODBUS_WIFI_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_GATEWAY_3
2069 | 1 | MODBUS_WIFI_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_GATEWAY_4
2070 | 1 | MODBUS_WIFI_MAC_ADDRESS_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_1
2071 | 1 | MODBUS_WIFI_MAC_ADDRESS_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_2
2072 | 1 | MODBUS_WIFI_MAC_ADDRESS_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_3
2073 | 1 | MODBUS_WIFI_MAC_ADDRESS_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_4
2074 | 1 | MODBUS_WIFI_MAC_ADDRESS_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_5
2075 | 1 | MODBUS_WIFI_MAC_ADDRESS_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_6
7100 | 2 | MODBUS_OUTPUT_VALUE_1 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | eg:high register 7100 . Low register 7101 Value = high_register*65536 + low_register If value is 12345 , all this value divide 1000 . calculate to three decimal places , that means 12.345
7102 | 2 | MODBUS_OUTPUT_VALUE_2 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_2
7104 | 2 | MODBUS_OUTPUT_VALUE_3 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_3
7106 | 2 | MODBUS_OUTPUT_VALUE_4 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_4
7108 | 2 | MODBUS_OUTPUT_VALUE_5 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_5
7110 | 2 | MODBUS_OUTPUT_VALUE_6 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_6
7112 | 2 | MODBUS_OUTPUT_VALUE_7 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_7
7114 | 2 | MODBUS_OUTPUT_VALUE_8 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_8
7116 | 2 | MODBUS_OUTPUT_VALUE_9 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_9
7118 | 2 | MODBUS_OUTPUT_VALUE_10 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_10
7120 | 2 | MODBUS_OUTPUT_VALUE_11 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_11
7122 | 2 | MODBUS_OUTPUT_VALUE_12 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_12
7124 | 2 | MODBUS_OUTPUT_VALUE_13 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_13
7126 | 2 | MODBUS_OUTPUT_VALUE_14 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_14
7128 | 2 | MODBUS_OUTPUT_VALUE_15 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_15
7130 | 2 | MODBUS_OUTPUT_VALUE_16 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_16
7132 | 2 | MODBUS_OUTPUT_VALUE_17 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_17
7134 | 2 | MODBUS_OUTPUT_VALUE_18 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_18
7136 | 2 | MODBUS_OUTPUT_VALUE_19 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_19
7138 | 2 | MODBUS_OUTPUT_VALUE_20 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_20
7140 | 2 | MODBUS_OUTPUT_VALUE_21 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_21
7142 | 2 | MODBUS_OUTPUT_VALUE_22 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_22
7144 | 2 | MODBUS_OUTPUT_VALUE_23 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_23
7146 | 2 | MODBUS_OUTPUT_VALUE_24 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_24
7148 | 2 | MODBUS_OUTPUT_VALUE_25 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_25
7150 | 2 | MODBUS_OUTPUT_VALUE_26 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_26
7152 | 2 | MODBUS_OUTPUT_VALUE_27 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_27
7154 | 2 | MODBUS_OUTPUT_VALUE_28 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_28
7156 | 2 | MODBUS_OUTPUT_VALUE_29 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_29
7158 | 2 | MODBUS_OUTPUT_VALUE_30 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_30
7160 | 2 | MODBUS_OUTPUT_VALUE_31 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_31
7162 | 2 | MODBUS_OUTPUT_VALUE_32 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_32
7164 | 2 | MODBUS_OUTPUT_VALUE_33 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_33
7166 | 2 | MODBUS_OUTPUT_VALUE_34 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_34
7168 | 2 | MODBUS_OUTPUT_VALUE_35 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_35
7170 | 2 | MODBUS_OUTPUT_VALUE_36 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_36
7172 | 2 | MODBUS_OUTPUT_VALUE_37 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_37
7174 | 2 | MODBUS_OUTPUT_VALUE_38 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_38
7176 | 2 | MODBUS_OUTPUT_VALUE_39 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_39
7178 | 2 | MODBUS_OUTPUT_VALUE_40 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_40
7180 | 2 | MODBUS_OUTPUT_VALUE_41 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_41
7182 | 2 | MODBUS_OUTPUT_VALUE_42 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_42
7184 | 2 | MODBUS_OUTPUT_VALUE_43 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_43
7186 | 2 | MODBUS_OUTPUT_VALUE_44 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_44
7188 | 2 | MODBUS_OUTPUT_VALUE_45 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_45
7190 | 2 | MODBUS_OUTPUT_VALUE_46 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_46
7192 | 2 | MODBUS_OUTPUT_VALUE_47 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_47
7194 | 2 | MODBUS_OUTPUT_VALUE_48 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_48
7196 | 2 | MODBUS_OUTPUT_VALUE_49 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_49
7198 | 2 | MODBUS_OUTPUT_VALUE_50 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_50
7200 | 2 | MODBUS_OUTPUT_VALUE_51 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_51
7202 | 2 | MODBUS_OUTPUT_VALUE_52 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_52
7204 | 2 | MODBUS_OUTPUT_VALUE_53 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_53
7206 | 2 | MODBUS_OUTPUT_VALUE_54 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_54
7208 | 2 | MODBUS_OUTPUT_VALUE_55 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_55
7210 | 2 | MODBUS_OUTPUT_VALUE_56 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_56
7212 | 2 | MODBUS_OUTPUT_VALUE_57 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_57
7214 | 2 | MODBUS_OUTPUT_VALUE_58 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_58
7216 | 2 | MODBUS_OUTPUT_VALUE_59 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_59
7218 | 2 | MODBUS_OUTPUT_VALUE_60 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_60
7220 | 2 | MODBUS_OUTPUT_VALUE_61 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_61
7222 | 2 | MODBUS_OUTPUT_VALUE_62 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_62
7224 | 2 | MODBUS_OUTPUT_VALUE_63 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_63
7226 | 2 | MODBUS_OUTPUT_VALUE_64 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_64
7228 | 1 | MODBUS_OUTPUT_SWICH_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output swith status (SW_OFF - 0, SW_AUTO - 1, SW_HAND - 2)
7229 | 1 | MODBUS_OUTPUT_SWICH_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_2
7230 | 1 | MODBUS_OUTPUT_SWICH_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_3
7231 | 1 | MODBUS_OUTPUT_SWICH_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_4
7232 | 1 | MODBUS_OUTPUT_SWICH_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_5
7233 | 1 | MODBUS_OUTPUT_SWICH_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_6
7234 | 1 | MODBUS_OUTPUT_SWICH_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_7
7235 | 1 | MODBUS_OUTPUT_SWICH_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_8
7236 | 1 | MODBUS_OUTPUT_SWICH_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_9
7237 | 1 | MODBUS_OUTPUT_SWICH_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_10
7238 | 1 | MODBUS_OUTPUT_SWICH_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_11
7239 | 1 | MODBUS_OUTPUT_SWICH_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_12
7240 | 1 | MODBUS_OUTPUT_SWICH_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_13
7241 | 1 | MODBUS_OUTPUT_SWICH_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_14
7242 | 1 | MODBUS_OUTPUT_SWICH_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_15
7243 | 1 | MODBUS_OUTPUT_SWICH_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_16
7244 | 1 | MODBUS_OUTPUT_SWICH_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_17
7245 | 1 | MODBUS_OUTPUT_SWICH_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_18
7246 | 1 | MODBUS_OUTPUT_SWICH_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_19
7247 | 1 | MODBUS_OUTPUT_SWICH_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_20
7248 | 1 | MODBUS_OUTPUT_SWICH_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_21
7249 | 1 | MODBUS_OUTPUT_SWICH_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_22
7250 | 1 | MODBUS_OUTPUT_SWICH_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_23
7251 | 1 | MODBUS_OUTPUT_SWICH_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_24
7252 | 1 | MODBUS_OUTPUT_SWICH_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_25
7253 | 1 | MODBUS_OUTPUT_SWICH_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_26
7254 | 1 | MODBUS_OUTPUT_SWICH_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_27
7255 | 1 | MODBUS_OUTPUT_SWICH_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_28
7256 | 1 | MODBUS_OUTPUT_SWICH_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_29
7257 | 1 | MODBUS_OUTPUT_SWICH_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_30
7258 | 1 | MODBUS_OUTPUT_SWICH_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_31
7259 | 1 | MODBUS_OUTPUT_SWICH_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_32
7260 | 1 | MODBUS_OUTPUT_SWICH_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_33
7261 | 1 | MODBUS_OUTPUT_SWICH_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_34
7262 | 1 | MODBUS_OUTPUT_SWICH_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_35
7263 | 1 | MODBUS_OUTPUT_SWICH_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_36
7264 | 1 | MODBUS_OUTPUT_SWICH_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_37
7265 | 1 | MODBUS_OUTPUT_SWICH_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_38
7266 | 1 | MODBUS_OUTPUT_SWICH_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_39
7267 | 1 | MODBUS_OUTPUT_SWICH_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_40
7268 | 1 | MODBUS_OUTPUT_SWICH_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_41
7269 | 1 | MODBUS_OUTPUT_SWICH_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_42
7270 | 1 | MODBUS_OUTPUT_SWICH_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_43
7271 | 1 | MODBUS_OUTPUT_SWICH_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_44
7272 | 1 | MODBUS_OUTPUT_SWICH_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_45
7273 | 1 | MODBUS_OUTPUT_SWICH_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_46
7274 | 1 | MODBUS_OUTPUT_SWICH_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_47
7275 | 1 | MODBUS_OUTPUT_SWICH_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_48
7276 | 1 | MODBUS_OUTPUT_SWICH_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_49
7277 | 1 | MODBUS_OUTPUT_SWICH_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_50
7278 | 1 | MODBUS_OUTPUT_SWICH_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_51
7279 | 1 | MODBUS_OUTPUT_SWICH_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_52
7280 | 1 | MODBUS_OUTPUT_SWICH_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_53
7281 | 1 | MODBUS_OUTPUT_SWICH_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_54
7282 | 1 | MODBUS_OUTPUT_SWICH_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_55
7283 | 1 | MODBUS_OUTPUT_SWICH_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_56
7284 | 1 | MODBUS_OUTPUT_SWICH_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_57
7285 | 1 | MODBUS_OUTPUT_SWICH_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_58
7286 | 1 | MODBUS_OUTPUT_SWICH_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_59
7287 | 1 | MODBUS_OUTPUT_SWICH_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_60
7288 | 1 | MODBUS_OUTPUT_SWICH_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_61
7289 | 1 | MODBUS_OUTPUT_SWICH_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_62
7290 | 1 | MODBUS_OUTPUT_SWICH_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_63
7291 | 1 | MODBUS_OUTPUT_SWICH_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_64
7292 | 1 | MODBUS_OUTPUT_RANGE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
7293 | 1 | MODBUS_OUTPUT_RANGE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_2
7294 | 1 | MODBUS_OUTPUT_RANGE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_3
7295 | 1 | MODBUS_OUTPUT_RANGE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_4
7296 | 1 | MODBUS_OUTPUT_RANGE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_5
7297 | 1 | MODBUS_OUTPUT_RANGE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_6
7298 | 1 | MODBUS_OUTPUT_RANGE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_7
7299 | 1 | MODBUS_OUTPUT_RANGE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_8
7300 | 1 | MODBUS_OUTPUT_RANGE_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_9
7301 | 1 | MODBUS_OUTPUT_RANGE_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_10
7302 | 1 | MODBUS_OUTPUT_RANGE_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_11
7303 | 1 | MODBUS_OUTPUT_RANGE_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_12
7304 | 1 | MODBUS_OUTPUT_RANGE_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_13
7305 | 1 | MODBUS_OUTPUT_RANGE_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_14
7306 | 1 | MODBUS_OUTPUT_RANGE_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_15
7307 | 1 | MODBUS_OUTPUT_RANGE_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_16
7308 | 1 | MODBUS_OUTPUT_RANGE_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_17
7309 | 1 | MODBUS_OUTPUT_RANGE_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_18
7310 | 1 | MODBUS_OUTPUT_RANGE_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_19
7311 | 1 | MODBUS_OUTPUT_RANGE_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_20
7312 | 1 | MODBUS_OUTPUT_RANGE_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_21
7313 | 1 | MODBUS_OUTPUT_RANGE_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_22
7314 | 1 | MODBUS_OUTPUT_RANGE_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_23
7315 | 1 | MODBUS_OUTPUT_RANGE_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_24
7316 | 1 | MODBUS_OUTPUT_RANGE_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_25
7317 | 1 | MODBUS_OUTPUT_RANGE_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_26
7318 | 1 | MODBUS_OUTPUT_RANGE_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_27
7319 | 1 | MODBUS_OUTPUT_RANGE_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_28
7320 | 1 | MODBUS_OUTPUT_RANGE_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_29
7321 | 1 | MODBUS_OUTPUT_RANGE_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_30
7322 | 1 | MODBUS_OUTPUT_RANGE_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_31
7323 | 1 | MODBUS_OUTPUT_RANGE_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_32
7324 | 1 | MODBUS_OUTPUT_RANGE_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_33
7325 | 1 | MODBUS_OUTPUT_RANGE_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_34
7326 | 1 | MODBUS_OUTPUT_RANGE_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_35
7327 | 1 | MODBUS_OUTPUT_RANGE_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_36
7328 | 1 | MODBUS_OUTPUT_RANGE_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_37
7329 | 1 | MODBUS_OUTPUT_RANGE_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_38
7330 | 1 | MODBUS_OUTPUT_RANGE_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_39
7331 | 1 | MODBUS_OUTPUT_RANGE_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_40
7332 | 1 | MODBUS_OUTPUT_RANGE_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_41
7333 | 1 | MODBUS_OUTPUT_RANGE_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_42
7334 | 1 | MODBUS_OUTPUT_RANGE_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_43
7335 | 1 | MODBUS_OUTPUT_RANGE_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_44
7336 | 1 | MODBUS_OUTPUT_RANGE_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_45
7337 | 1 | MODBUS_OUTPUT_RANGE_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_46
7338 | 1 | MODBUS_OUTPUT_RANGE_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_47
7339 | 1 | MODBUS_OUTPUT_RANGE_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_48
7340 | 1 | MODBUS_OUTPUT_RANGE_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_49
7341 | 1 | MODBUS_OUTPUT_RANGE_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_50
7342 | 1 | MODBUS_OUTPUT_RANGE_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_51
7343 | 1 | MODBUS_OUTPUT_RANGE_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_52
7344 | 1 | MODBUS_OUTPUT_RANGE_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_53
7345 | 1 | MODBUS_OUTPUT_RANGE_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_54
7346 | 1 | MODBUS_OUTPUT_RANGE_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_55
7347 | 1 | MODBUS_OUTPUT_RANGE_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_56
7348 | 1 | MODBUS_OUTPUT_RANGE_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_57
7349 | 1 | MODBUS_OUTPUT_RANGE_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_58
7350 | 1 | MODBUS_OUTPUT_RANGE_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_59
7351 | 1 | MODBUS_OUTPUT_RANGE_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_60
7352 | 1 | MODBUS_OUTPUT_RANGE_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_61
7353 | 1 | MODBUS_OUTPUT_RANGE_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_62
7354 | 1 | MODBUS_OUTPUT_RANGE_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_63
7355 | 1 | MODBUS_OUTPUT_RANGE_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_64
7356 | 1 | MODBUS_OUTPUT_AM_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output auto or manual (0 - auto, 1- manual)
7357 | 1 | MODBUS_OUTPUT_AM_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_2
7358 | 1 | MODBUS_OUTPUT_AM_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_3
7359 | 1 | MODBUS_OUTPUT_AM_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_4
7360 | 1 | MODBUS_OUTPUT_AM_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_5
7361 | 1 | MODBUS_OUTPUT_AM_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_6
7362 | 1 | MODBUS_OUTPUT_AM_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_7
7363 | 1 | MODBUS_OUTPUT_AM_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_8
7364 | 1 | MODBUS_OUTPUT_AM_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_9
7365 | 1 | MODBUS_OUTPUT_AM_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_10
7366 | 1 | MODBUS_OUTPUT_AM_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_11
7367 | 1 | MODBUS_OUTPUT_AM_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_12
7368 | 1 | MODBUS_OUTPUT_AM_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_13
7369 | 1 | MODBUS_OUTPUT_AM_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_14
7370 | 1 | MODBUS_OUTPUT_AM_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_15
7371 | 1 | MODBUS_OUTPUT_AM_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_16
7372 | 1 | MODBUS_OUTPUT_AM_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_17
7373 | 1 | MODBUS_OUTPUT_AM_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_18
7374 | 1 | MODBUS_OUTPUT_AM_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_19
7375 | 1 | MODBUS_OUTPUT_AM_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_20
7376 | 1 | MODBUS_OUTPUT_AM_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_21
7377 | 1 | MODBUS_OUTPUT_AM_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_22
7378 | 1 | MODBUS_OUTPUT_AM_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_23
7379 | 1 | MODBUS_OUTPUT_AM_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_24
7380 | 1 | MODBUS_OUTPUT_AM_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_25
7381 | 1 | MODBUS_OUTPUT_AM_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_26
7382 | 1 | MODBUS_OUTPUT_AM_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_27
7383 | 1 | MODBUS_OUTPUT_AM_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_28
7384 | 1 | MODBUS_OUTPUT_AM_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_29
7385 | 1 | MODBUS_OUTPUT_AM_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_30
7386 | 1 | MODBUS_OUTPUT_AM_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_31
7387 | 1 | MODBUS_OUTPUT_AM_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_32
7388 | 1 | MODBUS_OUTPUT_AM_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_33
7389 | 1 | MODBUS_OUTPUT_AM_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_34
7390 | 1 | MODBUS_OUTPUT_AM_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_35
7391 | 1 | MODBUS_OUTPUT_AM_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_36
7392 | 1 | MODBUS_OUTPUT_AM_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_37
7393 | 1 | MODBUS_OUTPUT_AM_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_38
7394 | 1 | MODBUS_OUTPUT_AM_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_39
7395 | 1 | MODBUS_OUTPUT_AM_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_40
7396 | 1 | MODBUS_OUTPUT_AM_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_41
7397 | 1 | MODBUS_OUTPUT_AM_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_42
7398 | 1 | MODBUS_OUTPUT_AM_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_43
7399 | 1 | MODBUS_OUTPUT_AM_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_44
7400 | 1 | MODBUS_OUTPUT_AM_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_45
7401 | 1 | MODBUS_OUTPUT_AM_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_46
7402 | 1 | MODBUS_OUTPUT_AM_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_47
7403 | 1 | MODBUS_OUTPUT_AM_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_48
7404 | 1 | MODBUS_OUTPUT_AM_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_49
7405 | 1 | MODBUS_OUTPUT_AM_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_50
7406 | 1 | MODBUS_OUTPUT_AM_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_51
7407 | 1 | MODBUS_OUTPUT_AM_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_52
7408 | 1 | MODBUS_OUTPUT_AM_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_53
7409 | 1 | MODBUS_OUTPUT_AM_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_54
7410 | 1 | MODBUS_OUTPUT_AM_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_55
7411 | 1 | MODBUS_OUTPUT_AM_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_56
7412 | 1 | MODBUS_OUTPUT_AM_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_57
7413 | 1 | MODBUS_OUTPUT_AM_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_58
7414 | 1 | MODBUS_OUTPUT_AM_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_59
7415 | 1 | MODBUS_OUTPUT_AM_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_60
7416 | 1 | MODBUS_OUTPUT_AM_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_61
7417 | 1 | MODBUS_OUTPUT_AM_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_62
7418 | 1 | MODBUS_OUTPUT_AM_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_63
7419 | 1 | MODBUS_OUTPUT_AM_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_64
7420 | 1 | MODBUS_OUTPUT_TYPE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output type, digital or analog (0 - digital 1 - analog)
7421 | 1 | MODBUS_OUTPUT_TYPE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_2
7422 | 1 | MODBUS_OUTPUT_TYPE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_3
7423 | 1 | MODBUS_OUTPUT_TYPE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_4
7424 | 1 | MODBUS_OUTPUT_TYPE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_5
7425 | 1 | MODBUS_OUTPUT_TYPE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_6
7426 | 1 | MODBUS_OUTPUT_TYPE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_7
7427 | 1 | MODBUS_OUTPUT_TYPE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_8
7428 | 1 | MODBUS_OUTPUT_TYPE_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_9
7429 | 1 | MODBUS_OUTPUT_TYPE_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_10
7430 | 1 | MODBUS_OUTPUT_TYPE_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_11
7431 | 1 | MODBUS_OUTPUT_TYPE_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_12
7432 | 1 | MODBUS_OUTPUT_TYPE_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_13
7433 | 1 | MODBUS_OUTPUT_TYPE_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_14
7434 | 1 | MODBUS_OUTPUT_TYPE_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_15
7435 | 1 | MODBUS_OUTPUT_TYPE_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_16
7436 | 1 | MODBUS_OUTPUT_TYPE_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_17
7437 | 1 | MODBUS_OUTPUT_TYPE_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_18
7438 | 1 | MODBUS_OUTPUT_TYPE_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_19
7439 | 1 | MODBUS_OUTPUT_TYPE_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_20
7440 | 1 | MODBUS_OUTPUT_TYPE_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_21
7441 | 1 | MODBUS_OUTPUT_TYPE_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_22
7442 | 1 | MODBUS_OUTPUT_TYPE_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_23
7443 | 1 | MODBUS_OUTPUT_TYPE_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_24
7444 | 1 | MODBUS_OUTPUT_TYPE_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_25
7445 | 1 | MODBUS_OUTPUT_TYPE_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_26
7446 | 1 | MODBUS_OUTPUT_TYPE_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_27
7447 | 1 | MODBUS_OUTPUT_TYPE_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_28
7448 | 1 | MODBUS_OUTPUT_TYPE_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_29
7449 | 1 | MODBUS_OUTPUT_TYPE_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_30
7450 | 1 | MODBUS_OUTPUT_TYPE_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_31
7451 | 1 | MODBUS_OUTPUT_TYPE_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_32
7452 | 1 | MODBUS_OUTPUT_TYPE_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_33
7453 | 1 | MODBUS_OUTPUT_TYPE_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_34
7454 | 1 | MODBUS_OUTPUT_TYPE_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_35
7455 | 1 | MODBUS_OUTPUT_TYPE_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_36
7456 | 1 | MODBUS_OUTPUT_TYPE_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_37
7457 | 1 | MODBUS_OUTPUT_TYPE_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_38
7458 | 1 | MODBUS_OUTPUT_TYPE_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_39
7459 | 1 | MODBUS_OUTPUT_TYPE_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_40
7460 | 1 | MODBUS_OUTPUT_TYPE_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_41
7461 | 1 | MODBUS_OUTPUT_TYPE_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_42
7462 | 1 | MODBUS_OUTPUT_TYPE_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_43
7463 | 1 | MODBUS_OUTPUT_TYPE_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_44
7464 | 1 | MODBUS_OUTPUT_TYPE_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_45
7465 | 1 | MODBUS_OUTPUT_TYPE_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_46
7466 | 1 | MODBUS_OUTPUT_TYPE_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_47
7467 | 1 | MODBUS_OUTPUT_TYPE_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_48
7468 | 1 | MODBUS_OUTPUT_TYPE_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_49
7469 | 1 | MODBUS_OUTPUT_TYPE_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_50
7470 | 1 | MODBUS_OUTPUT_TYPE_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_51
7471 | 1 | MODBUS_OUTPUT_TYPE_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_52
7472 | 1 | MODBUS_OUTPUT_TYPE_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_53
7473 | 1 | MODBUS_OUTPUT_TYPE_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_54
7474 | 1 | MODBUS_OUTPUT_TYPE_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_55
7475 | 1 | MODBUS_OUTPUT_TYPE_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_56
7476 | 1 | MODBUS_OUTPUT_TYPE_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_57
7477 | 1 | MODBUS_OUTPUT_TYPE_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_58
7478 | 1 | MODBUS_OUTPUT_TYPE_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_59
7479 | 1 | MODBUS_OUTPUT_TYPE_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_60
7480 | 1 | MODBUS_OUTPUT_TYPE_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_61
7481 | 1 | MODBUS_OUTPUT_TYPE_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_62
7482 | 1 | MODBUS_OUTPUT_TYPE_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_63
7483 | 1 | MODBUS_OUTPUT_TYPE_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_64
7484 | 2 | MODBUS_INPUT_VALUE_1 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_1 eg:high register 7484 . Low register 7485 Value = high_register*65536 + low_register If value is 12345 , all this value divide 1000 . calculate to three decimal places , that means 12.345
7486 | 2 | MODBUS_INPUT_VALUE_2 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_2
7488 | 2 | MODBUS_INPUT_VALUE_3 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_3
7490 | 2 | MODBUS_INPUT_VALUE_4 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_4
7492 | 2 | MODBUS_INPUT_VALUE_5 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_5
7494 | 2 | MODBUS_INPUT_VALUE_6 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_6
7496 | 2 | MODBUS_INPUT_VALUE_7 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_7
7498 | 2 | MODBUS_INPUT_VALUE_8 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_8
7500 | 2 | MODBUS_INPUT_VALUE_9 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_9
7502 | 2 | MODBUS_INPUT_VALUE_10 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_10
7504 | 2 | MODBUS_INPUT_VALUE_11 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_11
7506 | 2 | MODBUS_INPUT_VALUE_12 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_12
7508 | 2 | MODBUS_INPUT_VALUE_13 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_13
7510 | 2 | MODBUS_INPUT_VALUE_14 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_14
7512 | 2 | MODBUS_INPUT_VALUE_15 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_15
7514 | 2 | MODBUS_INPUT_VALUE_16 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_16
7516 | 2 | MODBUS_INPUT_VALUE_17 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_17
7518 | 2 | MODBUS_INPUT_VALUE_18 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_18
7520 | 2 | MODBUS_INPUT_VALUE_19 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_19
7522 | 2 | MODBUS_INPUT_VALUE_20 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_20
7524 | 2 | MODBUS_INPUT_VALUE_21 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_21
7526 | 2 | MODBUS_INPUT_VALUE_22 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_22
7528 | 2 | MODBUS_INPUT_VALUE_23 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_23
7530 | 2 | MODBUS_INPUT_VALUE_24 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_24
7532 | 2 | MODBUS_INPUT_VALUE_25 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_25
7534 | 2 | MODBUS_INPUT_VALUE_26 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_26
7536 | 2 | MODBUS_INPUT_VALUE_27 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_27
7538 | 2 | MODBUS_INPUT_VALUE_28 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_28
7540 | 2 | MODBUS_INPUT_VALUE_29 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_29
7542 | 2 | MODBUS_INPUT_VALUE_30 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_30
7544 | 2 | MODBUS_INPUT_VALUE_31 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_31
7546 | 2 | MODBUS_INPUT_VALUE_32 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_32
7548 | 2 | MODBUS_INPUT_VALUE_33 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_33
7550 | 2 | MODBUS_INPUT_VALUE_34 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_34
7552 | 2 | MODBUS_INPUT_VALUE_35 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_35
7554 | 2 | MODBUS_INPUT_VALUE_36 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_36
7556 | 2 | MODBUS_INPUT_VALUE_37 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_37
7558 | 2 | MODBUS_INPUT_VALUE_38 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_38
7560 | 2 | MODBUS_INPUT_VALUE_39 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_39
7562 | 2 | MODBUS_INPUT_VALUE_40 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_40
7564 | 2 | MODBUS_INPUT_VALUE_41 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_41
7566 | 2 | MODBUS_INPUT_VALUE_42 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_42
7568 | 2 | MODBUS_INPUT_VALUE_43 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_43
7570 | 2 | MODBUS_INPUT_VALUE_44 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_44
7572 | 2 | MODBUS_INPUT_VALUE_45 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_45
7574 | 2 | MODBUS_INPUT_VALUE_46 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_46
7576 | 2 | MODBUS_INPUT_VALUE_47 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_47
7578 | 2 | MODBUS_INPUT_VALUE_48 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_48
7580 | 2 | MODBUS_INPUT_VALUE_49 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_49
7582 | 2 | MODBUS_INPUT_VALUE_50 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_50
7584 | 2 | MODBUS_INPUT_VALUE_51 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_51
7586 | 2 | MODBUS_INPUT_VALUE_52 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_52
7588 | 2 | MODBUS_INPUT_VALUE_53 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_53
7590 | 2 | MODBUS_INPUT_VALUE_54 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_54
7592 | 2 | MODBUS_INPUT_VALUE_55 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_55
7594 | 2 | MODBUS_INPUT_VALUE_56 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_56
7596 | 2 | MODBUS_INPUT_VALUE_57 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_57
7598 | 2 | MODBUS_INPUT_VALUE_58 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_58
7600 | 2 | MODBUS_INPUT_VALUE_59 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_59
7602 | 2 | MODBUS_INPUT_VALUE_60 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_60
7604 | 2 | MODBUS_INPUT_VALUE_61 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_61
7606 | 2 | MODBUS_INPUT_VALUE_62 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_62
7608 | 2 | MODBUS_INPUT_VALUE_63 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_63
7610 | 2 | MODBUS_INPUT_VALUE_64 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_64
7612 | 1 | MODBUS_INPUT_FILTER_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_1
7613 | 1 | MODBUS_INPUT_FILTER_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_2
7614 | 1 | MODBUS_INPUT_FILTER_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_3
7615 | 1 | MODBUS_INPUT_FILTER_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_4
7616 | 1 | MODBUS_INPUT_FILTER_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_5
7617 | 1 | MODBUS_INPUT_FILTER_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_6
7618 | 1 | MODBUS_INPUT_FILTER_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_7
7619 | 1 | MODBUS_INPUT_FILTER_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_8
7620 | 1 | MODBUS_INPUT_FILTER_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_9
7621 | 1 | MODBUS_INPUT_FILTER_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_10
7622 | 1 | MODBUS_INPUT_FILTER_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_11
7623 | 1 | MODBUS_INPUT_FILTER_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_12
7624 | 1 | MODBUS_INPUT_FILTER_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_13
7625 | 1 | MODBUS_INPUT_FILTER_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_14
7626 | 1 | MODBUS_INPUT_FILTER_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_15
7627 | 1 | MODBUS_INPUT_FILTER_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_16
7628 | 1 | MODBUS_INPUT_FILTER_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_17
7629 | 1 | MODBUS_INPUT_FILTER_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_18
7630 | 1 | MODBUS_INPUT_FILTER_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_19
7631 | 1 | MODBUS_INPUT_FILTER_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_20
7632 | 1 | MODBUS_INPUT_FILTER_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_21
7633 | 1 | MODBUS_INPUT_FILTER_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_22
7634 | 1 | MODBUS_INPUT_FILTER_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_23
7635 | 1 | MODBUS_INPUT_FILTER_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_24
7636 | 1 | MODBUS_INPUT_FILTER_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_25
7637 | 1 | MODBUS_INPUT_FILTER_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_26
7638 | 1 | MODBUS_INPUT_FILTER_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_27
7639 | 1 | MODBUS_INPUT_FILTER_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_28
7640 | 1 | MODBUS_INPUT_FILTER_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_29
7641 | 1 | MODBUS_INPUT_FILTER_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_30
7642 | 1 | MODBUS_INPUT_FILTER_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_31
7643 | 1 | MODBUS_INPUT_FILTER_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_32
7644 | 1 | MODBUS_INPUT_FILTER_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_33
7645 | 1 | MODBUS_INPUT_FILTER_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_34
7646 | 1 | MODBUS_INPUT_FILTER_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_35
7647 | 1 | MODBUS_INPUT_FILTER_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_36
7648 | 1 | MODBUS_INPUT_FILTER_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_37
7649 | 1 | MODBUS_INPUT_FILTER_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_38
7650 | 1 | MODBUS_INPUT_FILTER_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_39
7651 | 1 | MODBUS_INPUT_FILTER_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_40
7652 | 1 | MODBUS_INPUT_FILTER_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_41
7653 | 1 | MODBUS_INPUT_FILTER_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_42
7654 | 1 | MODBUS_INPUT_FILTER_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_43
7655 | 1 | MODBUS_INPUT_FILTER_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_44
7656 | 1 | MODBUS_INPUT_FILTER_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_45
7657 | 1 | MODBUS_INPUT_FILTER_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_46
7658 | 1 | MODBUS_INPUT_FILTER_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_47
7659 | 1 | MODBUS_INPUT_FILTER_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_48
7660 | 1 | MODBUS_INPUT_FILTER_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_49
7661 | 1 | MODBUS_INPUT_FILTER_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_50
7662 | 1 | MODBUS_INPUT_FILTER_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_51
7663 | 1 | MODBUS_INPUT_FILTER_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_52
7664 | 1 | MODBUS_INPUT_FILTER_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_53
7665 | 1 | MODBUS_INPUT_FILTER_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_54
7666 | 1 | MODBUS_INPUT_FILTER_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_55
7667 | 1 | MODBUS_INPUT_FILTER_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_56
7668 | 1 | MODBUS_INPUT_FILTER_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_57
7669 | 1 | MODBUS_INPUT_FILTER_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_58
7670 | 1 | MODBUS_INPUT_FILTER_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_59
7671 | 1 | MODBUS_INPUT_FILTER_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_60
7672 | 1 | MODBUS_INPUT_FILTER_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_61
7673 | 1 | MODBUS_INPUT_FILTER_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_62
7674 | 1 | MODBUS_INPUT_FILTER_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_63
7675 | 1 | MODBUS_INPUT_FILTER_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_64
7676 | 1 | MODBUS_INPUT_CALIBRATION_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_1
7677 | 1 | MODBUS_INPUT_CALIBRATION_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_2
7678 | 1 | MODBUS_INPUT_CALIBRATION_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_3
7679 | 1 | MODBUS_INPUT_CALIBRATION_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_4
7680 | 1 | MODBUS_INPUT_CALIBRATION_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_5
7681 | 1 | MODBUS_INPUT_CALIBRATION_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_6
7682 | 1 | MODBUS_INPUT_CALIBRATION_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_7
7683 | 1 | MODBUS_INPUT_CALIBRATION_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_8
7684 | 1 | MODBUS_INPUT_CALIBRATION_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_9
7685 | 1 | MODBUS_INPUT_CALIBRATION_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_10
7686 | 1 | MODBUS_INPUT_CALIBRATION_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_11
7687 | 1 | MODBUS_INPUT_CALIBRATION_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_12
7688 | 1 | MODBUS_INPUT_CALIBRATION_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_13
7689 | 1 | MODBUS_INPUT_CALIBRATION_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_14
7690 | 1 | MODBUS_INPUT_CALIBRATION_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_15
7691 | 1 | MODBUS_INPUT_CALIBRATION_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_16
7692 | 1 | MODBUS_INPUT_CALIBRATION_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_17
7693 | 1 | MODBUS_INPUT_CALIBRATION_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_18
7694 | 1 | MODBUS_INPUT_CALIBRATION_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_19
7695 | 1 | MODBUS_INPUT_CALIBRATION_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_20
7696 | 1 | MODBUS_INPUT_CALIBRATION_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_21
7697 | 1 | MODBUS_INPUT_CALIBRATION_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_22
7698 | 1 | MODBUS_INPUT_CALIBRATION_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_23
7699 | 1 | MODBUS_INPUT_CALIBRATION_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_24
7700 | 1 | MODBUS_INPUT_CALIBRATION_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_25
7701 | 1 | MODBUS_INPUT_CALIBRATION_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_26
7702 | 1 | MODBUS_INPUT_CALIBRATION_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_27
7703 | 1 | MODBUS_INPUT_CALIBRATION_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_28
7704 | 1 | MODBUS_INPUT_CALIBRATION_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_29
7705 | 1 | MODBUS_INPUT_CALIBRATION_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_30
7706 | 1 | MODBUS_INPUT_CALIBRATION_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_31
7707 | 1 | MODBUS_INPUT_CALIBRATION_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_32
7708 | 1 | MODBUS_INPUT_CALIBRATION_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_33
7709 | 1 | MODBUS_INPUT_CALIBRATION_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_34
7710 | 1 | MODBUS_INPUT_CALIBRATION_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_35
7711 | 1 | MODBUS_INPUT_CALIBRATION_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_36
7712 | 1 | MODBUS_INPUT_CALIBRATION_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_37
7713 | 1 | MODBUS_INPUT_CALIBRATION_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_38
7714 | 1 | MODBUS_INPUT_CALIBRATION_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_39
7715 | 1 | MODBUS_INPUT_CALIBRATION_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_40
7716 | 1 | MODBUS_INPUT_CALIBRATION_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_41
7717 | 1 | MODBUS_INPUT_CALIBRATION_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_42
7718 | 1 | MODBUS_INPUT_CALIBRATION_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_43
7719 | 1 | MODBUS_INPUT_CALIBRATION_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_44
7720 | 1 | MODBUS_INPUT_CALIBRATION_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_45
7721 | 1 | MODBUS_INPUT_CALIBRATION_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_46
7722 | 1 | MODBUS_INPUT_CALIBRATION_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_47
7723 | 1 | MODBUS_INPUT_CALIBRATION_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_48
7724 | 1 | MODBUS_INPUT_CALIBRATION_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_49
7725 | 1 | MODBUS_INPUT_CALIBRATION_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_50
7726 | 1 | MODBUS_INPUT_CALIBRATION_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_51
7727 | 1 | MODBUS_INPUT_CALIBRATION_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_52
7728 | 1 | MODBUS_INPUT_CALIBRATION_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_53
7729 | 1 | MODBUS_INPUT_CALIBRATION_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_54
7730 | 1 | MODBUS_INPUT_CALIBRATION_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_55
7731 | 1 | MODBUS_INPUT_CALIBRATION_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_56
7732 | 1 | MODBUS_INPUT_CALIBRATION_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_57
7733 | 1 | MODBUS_INPUT_CALIBRATION_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_58
7734 | 1 | MODBUS_INPUT_CALIBRATION_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_59
7735 | 1 | MODBUS_INPUT_CALIBRATION_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_60
7736 | 1 | MODBUS_INPUT_CALIBRATION_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_61
7737 | 1 | MODBUS_INPUT_CALIBRATION_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_62
7738 | 1 | MODBUS_INPUT_CALIBRATION_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_63
7739 | 1 | MODBUS_INPUT_CALIBRATION_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_64
7740 | 1 | MODBUS_INPUT_CAL_SIGN_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_1
7741 | 1 | MODBUS_INPUT_CAL_SIGN_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_2
7742 | 1 | MODBUS_INPUT_CAL_SIGN_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_3
7743 | 1 | MODBUS_INPUT_CAL_SIGN_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_4
7744 | 1 | MODBUS_INPUT_CAL_SIGN_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_5
7745 | 1 | MODBUS_INPUT_CAL_SIGN_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_6
7746 | 1 | MODBUS_INPUT_CAL_SIGN_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_7
7747 | 1 | MODBUS_INPUT_CAL_SIGN_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_8
7748 | 1 | MODBUS_INPUT_CAL_SIGN_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_9
7749 | 1 | MODBUS_INPUT_CAL_SIGN_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_10
7750 | 1 | MODBUS_INPUT_CAL_SIGN_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_11
7751 | 1 | MODBUS_INPUT_CAL_SIGN_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_12
7752 | 1 | MODBUS_INPUT_CAL_SIGN_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_13
7753 | 1 | MODBUS_INPUT_CAL_SIGN_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_14
7754 | 1 | MODBUS_INPUT_CAL_SIGN_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_15
7755 | 1 | MODBUS_INPUT_CAL_SIGN_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_16
7756 | 1 | MODBUS_INPUT_CAL_SIGN_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_17
7757 | 1 | MODBUS_INPUT_CAL_SIGN_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_18
7758 | 1 | MODBUS_INPUT_CAL_SIGN_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_19
7759 | 1 | MODBUS_INPUT_CAL_SIGN_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_20
7760 | 1 | MODBUS_INPUT_CAL_SIGN_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_21
7761 | 1 | MODBUS_INPUT_CAL_SIGN_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_22
7762 | 1 | MODBUS_INPUT_CAL_SIGN_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_23
7763 | 1 | MODBUS_INPUT_CAL_SIGN_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_24
7764 | 1 | MODBUS_INPUT_CAL_SIGN_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_25
7765 | 1 | MODBUS_INPUT_CAL_SIGN_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_26
7766 | 1 | MODBUS_INPUT_CAL_SIGN_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_27
7767 | 1 | MODBUS_INPUT_CAL_SIGN_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_28
7768 | 1 | MODBUS_INPUT_CAL_SIGN_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_29
7769 | 1 | MODBUS_INPUT_CAL_SIGN_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_30
7770 | 1 | MODBUS_INPUT_CAL_SIGN_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_31
7771 | 1 | MODBUS_INPUT_CAL_SIGN_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_32
7772 | 1 | MODBUS_INPUT_CAL_SIGN_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_33
7773 | 1 | MODBUS_INPUT_CAL_SIGN_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_34
7774 | 1 | MODBUS_INPUT_CAL_SIGN_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_35
7775 | 1 | MODBUS_INPUT_CAL_SIGN_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_36
7776 | 1 | MODBUS_INPUT_CAL_SIGN_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_37
7777 | 1 | MODBUS_INPUT_CAL_SIGN_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_38
7778 | 1 | MODBUS_INPUT_CAL_SIGN_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_39
7779 | 1 | MODBUS_INPUT_CAL_SIGN_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_40
7780 | 1 | MODBUS_INPUT_CAL_SIGN_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_41
7781 | 1 | MODBUS_INPUT_CAL_SIGN_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_42
7782 | 1 | MODBUS_INPUT_CAL_SIGN_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_43
7783 | 1 | MODBUS_INPUT_CAL_SIGN_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_44
7784 | 1 | MODBUS_INPUT_CAL_SIGN_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_45
7785 | 1 | MODBUS_INPUT_CAL_SIGN_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_46
7786 | 1 | MODBUS_INPUT_CAL_SIGN_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_47
7787 | 1 | MODBUS_INPUT_CAL_SIGN_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_48
7788 | 1 | MODBUS_INPUT_CAL_SIGN_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_49
7789 | 1 | MODBUS_INPUT_CAL_SIGN_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_50
7790 | 1 | MODBUS_INPUT_CAL_SIGN_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_51
7791 | 1 | MODBUS_INPUT_CAL_SIGN_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_52
7792 | 1 | MODBUS_INPUT_CAL_SIGN_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_53
7793 | 1 | MODBUS_INPUT_CAL_SIGN_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_54
7794 | 1 | MODBUS_INPUT_CAL_SIGN_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_55
7795 | 1 | MODBUS_INPUT_CAL_SIGN_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_56
7796 | 1 | MODBUS_INPUT_CAL_SIGN_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_57
7797 | 1 | MODBUS_INPUT_CAL_SIGN_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_58
7798 | 1 | MODBUS_INPUT_CAL_SIGN_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_59
7799 | 1 | MODBUS_INPUT_CAL_SIGN_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_60
7800 | 1 | MODBUS_INPUT_CAL_SIGN_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_61
7801 | 1 | MODBUS_INPUT_CAL_SIGN_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_62
7802 | 1 | MODBUS_INPUT_CAL_SIGN_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_63
7803 | 1 | MODBUS_INPUT_CAL_SIGN_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_64
7804 | 1 | MODBUS_INPUT_RANGE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | high bye is analog or digital (digital is 0, analog is 1), low byte is range. if analog inputs (not_used_input = 0, Y3K_40_150DegC, Y3K_40_300DegF, R10K_40_120DegC, R10K_40_250DegF, R3K_40_150DegC, R3K_40_300DegF, KM10K_40_120DegC, KM10K_40_250DegF, A10K_50_110DegC, A10K_60_200DegF, V0_5, I0_100Amps, I0_20ma, I0_20psi, N0_2_32counts, N0_3000FPM_0_5V, P0_100_0_5V, P0_100_4_20ma, P0_255p_min, table1, table2, table3, table4, table5,100 - HI_SPEED_COUNTER ),
7805 | 1 | MODBUS_INPUT_RANGE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | if digital inputs not_used_input = 0 OFF_ON = 1, CLOSED_OPEN = 2, STOP_START = 3, DISABLED_ENABLED = 4, NORMAL_ALARM = 5, NORMAL_HIGH = 6, NORMAL_LOW = 7, NO_YES = 8, COOL_HEAT = 9, UNOCCUPIED_OCCUPIED = 10, LOW_HIGH = 11, ON_OFF = 12 , OPEN_CLOSED, START_STOP, ENABLED_DISABLED, ALARM_NORMAL, HIGH_NORMAL, LOW_NORMAL, YES_NO, HEAT_COOL, OCCUPIED_UNOCCUPIED, HIGH_LOW, custom_digital1, custom_digital2, custom_digital3, custom_digital4, custom_digital5, custom_digital6, custom_digital7, custom_digital8 )
7806 | 1 | MODBUS_INPUT_RANGE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_3
7807 | 1 | MODBUS_INPUT_RANGE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_4
7808 | 1 | MODBUS_INPUT_RANGE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_5
7809 | 1 | MODBUS_INPUT_RANGE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_6
7810 | 1 | MODBUS_INPUT_RANGE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_7
7811 | 1 | MODBUS_INPUT_RANGE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_8
7812 | 1 | MODBUS_INPUT_RANGE_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_9
7813 | 1 | MODBUS_INPUT_RANGE_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_10
7814 | 1 | MODBUS_INPUT_RANGE_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_11
7815 | 1 | MODBUS_INPUT_RANGE_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_12
7816 | 1 | MODBUS_INPUT_RANGE_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_13
7817 | 1 | MODBUS_INPUT_RANGE_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_14
7818 | 1 | MODBUS_INPUT_RANGE_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_15
7819 | 1 | MODBUS_INPUT_RANGE_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_16
7820 | 1 | MODBUS_INPUT_RANGE_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_17
7821 | 1 | MODBUS_INPUT_RANGE_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_18
7822 | 1 | MODBUS_INPUT_RANGE_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_19
7823 | 1 | MODBUS_INPUT_RANGE_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_20
7824 | 1 | MODBUS_INPUT_RANGE_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_21
7825 | 1 | MODBUS_INPUT_RANGE_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_22
7826 | 1 | MODBUS_INPUT_RANGE_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_23
7827 | 1 | MODBUS_INPUT_RANGE_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_24
7828 | 1 | MODBUS_INPUT_RANGE_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_25
7829 | 1 | MODBUS_INPUT_RANGE_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_26
7830 | 1 | MODBUS_INPUT_RANGE_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_27
7831 | 1 | MODBUS_INPUT_RANGE_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_28
7832 | 1 | MODBUS_INPUT_RANGE_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_29
7833 | 1 | MODBUS_INPUT_RANGE_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_30
7834 | 1 | MODBUS_INPUT_RANGE_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_31
7835 | 1 | MODBUS_INPUT_RANGE_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_32
7836 | 1 | MODBUS_INPUT_RANGE_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_33
7837 | 1 | MODBUS_INPUT_RANGE_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_34
7838 | 1 | MODBUS_INPUT_RANGE_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_35
7839 | 1 | MODBUS_INPUT_RANGE_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_36
7840 | 1 | MODBUS_INPUT_RANGE_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_37
7841 | 1 | MODBUS_INPUT_RANGE_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_38
7842 | 1 | MODBUS_INPUT_RANGE_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_39
7843 | 1 | MODBUS_INPUT_RANGE_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_40
7844 | 1 | MODBUS_INPUT_RANGE_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_41
7845 | 1 | MODBUS_INPUT_RANGE_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_42
7846 | 1 | MODBUS_INPUT_RANGE_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_43
7847 | 1 | MODBUS_INPUT_RANGE_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_44
7848 | 1 | MODBUS_INPUT_RANGE_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_45
7849 | 1 | MODBUS_INPUT_RANGE_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_46
7850 | 1 | MODBUS_INPUT_RANGE_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_47
7851 | 1 | MODBUS_INPUT_RANGE_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_48
7852 | 1 | MODBUS_INPUT_RANGE_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_49
7853 | 1 | MODBUS_INPUT_RANGE_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_50
7854 | 1 | MODBUS_INPUT_RANGE_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_51
7855 | 1 | MODBUS_INPUT_RANGE_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_52
7856 | 1 | MODBUS_INPUT_RANGE_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_53
7857 | 1 | MODBUS_INPUT_RANGE_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_54
7858 | 1 | MODBUS_INPUT_RANGE_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_55
7859 | 1 | MODBUS_INPUT_RANGE_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_56
7860 | 1 | MODBUS_INPUT_RANGE_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_57
7861 | 1 | MODBUS_INPUT_RANGE_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_58
7862 | 1 | MODBUS_INPUT_RANGE_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_59
7863 | 1 | MODBUS_INPUT_RANGE_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_60
7864 | 1 | MODBUS_INPUT_RANGE_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_61
7865 | 1 | MODBUS_INPUT_RANGE_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_62
7866 | 1 | MODBUS_INPUT_RANGE_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_63
7867 | 1 | MODBUS_INPUT_RANGE_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_64
7868 | 1 | MODBUS_INPUT_AM_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Auto or Maunual of inputs
7869 | 1 | MODBUS_INPUT_AM_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_2
7870 | 1 | MODBUS_INPUT_AM_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_3
7871 | 1 | MODBUS_INPUT_AM_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_4
7872 | 1 | MODBUS_INPUT_AM_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_5
7873 | 1 | MODBUS_INPUT_AM_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_6
7874 | 1 | MODBUS_INPUT_AM_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_7
7875 | 1 | MODBUS_INPUT_AM_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_8
7876 | 1 | MODBUS_INPUT_AM_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_9
7877 | 1 | MODBUS_INPUT_AM_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_10
7878 | 1 | MODBUS_INPUT_AM_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_11
7879 | 1 | MODBUS_INPUT_AM_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_12
7880 | 1 | MODBUS_INPUT_AM_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_13
7881 | 1 | MODBUS_INPUT_AM_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_14
7882 | 1 | MODBUS_INPUT_AM_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_15
7883 | 1 | MODBUS_INPUT_AM_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_16
7884 | 1 | MODBUS_INPUT_AM_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_17
7885 | 1 | MODBUS_INPUT_AM_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_18
7886 | 1 | MODBUS_INPUT_AM_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_19
7887 | 1 | MODBUS_INPUT_AM_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_20
7888 | 1 | MODBUS_INPUT_AM_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_21
7889 | 1 | MODBUS_INPUT_AM_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_22
7890 | 1 | MODBUS_INPUT_AM_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_23
7891 | 1 | MODBUS_INPUT_AM_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_24
7892 | 1 | MODBUS_INPUT_AM_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_25
7893 | 1 | MODBUS_INPUT_AM_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_26
7894 | 1 | MODBUS_INPUT_AM_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_27
7895 | 1 | MODBUS_INPUT_AM_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_28
7896 | 1 | MODBUS_INPUT_AM_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_29
7897 | 1 | MODBUS_INPUT_AM_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_30
7898 | 1 | MODBUS_INPUT_AM_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_31
7899 | 1 | MODBUS_INPUT_AM_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_32
7900 | 1 | MODBUS_INPUT_AM_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_33
7901 | 1 | MODBUS_INPUT_AM_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_34
7902 | 1 | MODBUS_INPUT_AM_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_35
7903 | 1 | MODBUS_INPUT_AM_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_36
7904 | 1 | MODBUS_INPUT_AM_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_37
7905 | 1 | MODBUS_INPUT_AM_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_38
7906 | 1 | MODBUS_INPUT_AM_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_39
7907 | 1 | MODBUS_INPUT_AM_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_40
7908 | 1 | MODBUS_INPUT_AM_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_41
7909 | 1 | MODBUS_INPUT_AM_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_42
7910 | 1 | MODBUS_INPUT_AM_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_43
7911 | 1 | MODBUS_INPUT_AM_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_44
7912 | 1 | MODBUS_INPUT_AM_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_45
7913 | 1 | MODBUS_INPUT_AM_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_46
7914 | 1 | MODBUS_INPUT_AM_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_47
7915 | 1 | MODBUS_INPUT_AM_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_48
7916 | 1 | MODBUS_INPUT_AM_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_49
7917 | 1 | MODBUS_INPUT_AM_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_50
7918 | 1 | MODBUS_INPUT_AM_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_51
7919 | 1 | MODBUS_INPUT_AM_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_52
7920 | 1 | MODBUS_INPUT_AM_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_53
7921 | 1 | MODBUS_INPUT_AM_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_54
7922 | 1 | MODBUS_INPUT_AM_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_55
7923 | 1 | MODBUS_INPUT_AM_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_56
7924 | 1 | MODBUS_INPUT_AM_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_57
7925 | 1 | MODBUS_INPUT_AM_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_58
7926 | 1 | MODBUS_INPUT_AM_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_59
7927 | 1 | MODBUS_INPUT_AM_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_60
7928 | 1 | MODBUS_INPUT_AM_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_61
7929 | 1 | MODBUS_INPUT_AM_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_62
7930 | 1 | MODBUS_INPUT_AM_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_63
7931 | 1 | MODBUS_INPUT_AM_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_64
7932 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_1 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_1
7934 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_2 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_2
7936 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_3 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_3
7938 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_4 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_4
7940 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_5 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_5
7942 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_6 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_6
7944 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_7 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_7
7946 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_8 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_8
7948 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_9 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_9
7950 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_10 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_10
7952 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_11 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_11
7954 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_12 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_12
7956 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_13 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_13
7958 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_14 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_14
7960 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_15 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_15
7962 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_16 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_16
7964 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_17 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_17
7966 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_18 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_18
7968 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_19 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_19
7970 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_20 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_20
7972 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_21 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_21
7974 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_22 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_22
7976 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_23 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_23
7978 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_24 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_24
7980 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_25 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_25
7982 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_26 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_26
7984 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_27 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_27
7986 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_28 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_28
7988 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_29 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_29
7990 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_30 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_30
7992 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_31 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_31
7994 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_32 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_32
7996 | 1 | MODBUS_INPUT_HI_SPD_EN_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ENABLE high speed counter,( START - 0, STOP - 1)
7997 | 1 | MODBUS_INPUT_HI_SPD_EN_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_2
7998 | 1 | MODBUS_INPUT_HI_SPD_EN_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_3
7999 | 1 | MODBUS_INPUT_HI_SPD_EN_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_4
8000 | 1 | MODBUS_INPUT_HI_SPD_EN_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_5
8001 | 1 | MODBUS_INPUT_HI_SPD_EN_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_6
8002 | 1 | MODBUS_INPUT_HI_SPD_EN_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_7
8003 | 1 | MODBUS_INPUT_HI_SPD_EN_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_8
8004 | 1 | MODBUS_INPUT_HI_SPD_EN_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_9
8005 | 1 | MODBUS_INPUT_HI_SPD_EN_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_10
8006 | 1 | MODBUS_INPUT_HI_SPD_EN_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_11
8007 | 1 | MODBUS_INPUT_HI_SPD_EN_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_12
8008 | 1 | MODBUS_INPUT_HI_SPD_EN_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_13
8009 | 1 | MODBUS_INPUT_HI_SPD_EN_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_14
8010 | 1 | MODBUS_INPUT_HI_SPD_EN_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_15
8011 | 1 | MODBUS_INPUT_HI_SPD_EN_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_16
8012 | 1 | MODBUS_INPUT_HI_SPD_EN_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_17
8013 | 1 | MODBUS_INPUT_HI_SPD_EN_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_18
8014 | 1 | MODBUS_INPUT_HI_SPD_EN_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_19
8015 | 1 | MODBUS_INPUT_HI_SPD_EN_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_20
8016 | 1 | MODBUS_INPUT_HI_SPD_EN_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_21
8017 | 1 | MODBUS_INPUT_HI_SPD_EN_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_22
8018 | 1 | MODBUS_INPUT_HI_SPD_EN_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_23
8019 | 1 | MODBUS_INPUT_HI_SPD_EN_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_24
8020 | 1 | MODBUS_INPUT_HI_SPD_EN_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_25
8021 | 1 | MODBUS_INPUT_HI_SPD_EN_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_26
8022 | 1 | MODBUS_INPUT_HI_SPD_EN_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_27
8023 | 1 | MODBUS_INPUT_HI_SPD_EN_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_28
8024 | 1 | MODBUS_INPUT_HI_SPD_EN_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_29
8025 | 1 | MODBUS_INPUT_HI_SPD_EN_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_30
8026 | 1 | MODBUS_INPUT_HI_SPD_EN_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_31
8027 | 1 | MODBUS_INPUT_HI_SPD_EN_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_32
8028 | 1 | MODBUS_INPUT_TYPE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Input type, 0- thermistor, 1- 5v, 2-10v, 3- 20ma
8029 | 1 | MODBUS_INPUT_TYPE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_2
8030 | 1 | MODBUS_INPUT_TYPE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_3
8031 | 1 | MODBUS_INPUT_TYPE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_4
8032 | 1 | MODBUS_INPUT_TYPE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_5
8033 | 1 | MODBUS_INPUT_TYPE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_6
8034 | 1 | MODBUS_INPUT_TYPE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_7
8035 | 1 | MODBUS_INPUT_TYPE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_8
8036 | 1 | MODBUS_INPUT_TYPE_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_9
8037 | 1 | MODBUS_INPUT_TYPE_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_10
8038 | 1 | MODBUS_INPUT_TYPE_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_11
8039 | 1 | MODBUS_INPUT_TYPE_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_12
8040 | 1 | MODBUS_INPUT_TYPE_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_13
8041 | 1 | MODBUS_INPUT_TYPE_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_14
8042 | 1 | MODBUS_INPUT_TYPE_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_15
8043 | 1 | MODBUS_INPUT_TYPE_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_16
8044 | 1 | MODBUS_INPUT_TYPE_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_17
8045 | 1 | MODBUS_INPUT_TYPE_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_18
8046 | 1 | MODBUS_INPUT_TYPE_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_19
8047 | 1 | MODBUS_INPUT_TYPE_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_20
8048 | 1 | MODBUS_INPUT_TYPE_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_21
8049 | 1 | MODBUS_INPUT_TYPE_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_22
8050 | 1 | MODBUS_INPUT_TYPE_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_23
8051 | 1 | MODBUS_INPUT_TYPE_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_24
8052 | 1 | MODBUS_INPUT_TYPE_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_25
8053 | 1 | MODBUS_INPUT_TYPE_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_26
8054 | 1 | MODBUS_INPUT_TYPE_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_27
8055 | 1 | MODBUS_INPUT_TYPE_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_28
8056 | 1 | MODBUS_INPUT_TYPE_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_29
8057 | 1 | MODBUS_INPUT_TYPE_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_30
8058 | 1 | MODBUS_INPUT_TYPE_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_31
8059 | 1 | MODBUS_INPUT_TYPE_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_32
8060 | 1 | MODBUS_INPUT_TYPE_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_33
8061 | 1 | MODBUS_INPUT_TYPE_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_34
8062 | 1 | MODBUS_INPUT_TYPE_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_35
8063 | 1 | MODBUS_INPUT_TYPE_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_36
8064 | 1 | MODBUS_INPUT_TYPE_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_37
8065 | 1 | MODBUS_INPUT_TYPE_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_38
8066 | 1 | MODBUS_INPUT_TYPE_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_39
8067 | 1 | MODBUS_INPUT_TYPE_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_40
8068 | 1 | MODBUS_INPUT_TYPE_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_41
8069 | 1 | MODBUS_INPUT_TYPE_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_42
8070 | 1 | MODBUS_INPUT_TYPE_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_43
8071 | 1 | MODBUS_INPUT_TYPE_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_44
8072 | 1 | MODBUS_INPUT_TYPE_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_45
8073 | 1 | MODBUS_INPUT_TYPE_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_46
8074 | 1 | MODBUS_INPUT_TYPE_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_47
8075 | 1 | MODBUS_INPUT_TYPE_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_48
8076 | 1 | MODBUS_INPUT_TYPE_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_49
8077 | 1 | MODBUS_INPUT_TYPE_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_50
8078 | 1 | MODBUS_INPUT_TYPE_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_51
8079 | 1 | MODBUS_INPUT_TYPE_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_52
8080 | 1 | MODBUS_INPUT_TYPE_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_53
8081 | 1 | MODBUS_INPUT_TYPE_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_54
8082 | 1 | MODBUS_INPUT_TYPE_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_55
8083 | 1 | MODBUS_INPUT_TYPE_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_56
8084 | 1 | MODBUS_INPUT_TYPE_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_57
8085 | 1 | MODBUS_INPUT_TYPE_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_58
8086 | 1 | MODBUS_INPUT_TYPE_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_59
8087 | 1 | MODBUS_INPUT_TYPE_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_60
8088 | 1 | MODBUS_INPUT_TYPE_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_61
8089 | 1 | MODBUS_INPUT_TYPE_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_62
8090 | 1 | MODBUS_INPUT_TYPE_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_63
8091 | 1 | MODBUS_INPUT_TYPE_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_64
8092 | 2 | MODBUS_VAR_VALUE_1 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_1 eg:high register 8092 . Low register 8093 Value = high_register*65536 + low_register If value is 12345 , all this value divide 1000 . calculate to three decimal places , that means 12.345
8094 | 2 | MODBUS_VAR_VALUE_2 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_2
8096 | 2 | MODBUS_VAR_VALUE_3 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_3
8098 | 2 | MODBUS_VAR_VALUE_4 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_4
8100 | 2 | MODBUS_VAR_VALUE_5 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_5
8102 | 2 | MODBUS_VAR_VALUE_6 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_6
8104 | 2 | MODBUS_VAR_VALUE_7 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_7
8106 | 2 | MODBUS_VAR_VALUE_8 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_8
8108 | 2 | MODBUS_VAR_VALUE_9 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_9
8110 | 2 | MODBUS_VAR_VALUE_10 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_10
8112 | 2 | MODBUS_VAR_VALUE_11 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_11
8114 | 2 | MODBUS_VAR_VALUE_12 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_12
8116 | 2 | MODBUS_VAR_VALUE_13 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_13
8118 | 2 | MODBUS_VAR_VALUE_14 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_14
8120 | 2 | MODBUS_VAR_VALUE_15 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_15
8122 | 2 | MODBUS_VAR_VALUE_16 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_16
8124 | 2 | MODBUS_VAR_VALUE_17 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_17
8126 | 2 | MODBUS_VAR_VALUE_18 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_18
8128 | 2 | MODBUS_VAR_VALUE_19 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_19
8130 | 2 | MODBUS_VAR_VALUE_20 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_20
8132 | 2 | MODBUS_VAR_VALUE_21 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_21
8134 | 2 | MODBUS_VAR_VALUE_22 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_22
8136 | 2 | MODBUS_VAR_VALUE_23 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_23
8138 | 2 | MODBUS_VAR_VALUE_24 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_24
8140 | 2 | MODBUS_VAR_VALUE_25 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_25
8142 | 2 | MODBUS_VAR_VALUE_26 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_26
8144 | 2 | MODBUS_VAR_VALUE_27 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_27
8146 | 2 | MODBUS_VAR_VALUE_28 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_28
8148 | 2 | MODBUS_VAR_VALUE_29 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_29
8150 | 2 | MODBUS_VAR_VALUE_30 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_30
8152 | 2 | MODBUS_VAR_VALUE_31 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_31
8154 | 2 | MODBUS_VAR_VALUE_32 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_32
8156 | 2 | MODBUS_VAR_VALUE_33 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_33
8158 | 2 | MODBUS_VAR_VALUE_34 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_34
8160 | 2 | MODBUS_VAR_VALUE_35 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_35
8162 | 2 | MODBUS_VAR_VALUE_36 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_36
8164 | 2 | MODBUS_VAR_VALUE_37 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_37
8166 | 2 | MODBUS_VAR_VALUE_38 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_38
8168 | 2 | MODBUS_VAR_VALUE_39 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_39
8170 | 2 | MODBUS_VAR_VALUE_40 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_40
8172 | 2 | MODBUS_VAR_VALUE_41 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_41
8174 | 2 | MODBUS_VAR_VALUE_42 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_42
8176 | 2 | MODBUS_VAR_VALUE_43 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_43
8178 | 2 | MODBUS_VAR_VALUE_44 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_44
8180 | 2 | MODBUS_VAR_VALUE_45 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_45
8182 | 2 | MODBUS_VAR_VALUE_46 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_46
8184 | 2 | MODBUS_VAR_VALUE_47 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_47
8186 | 2 | MODBUS_VAR_VALUE_48 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_48
8188 | 2 | MODBUS_VAR_VALUE_49 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_49
8190 | 2 | MODBUS_VAR_VALUE_50 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_50
8192 | 2 | MODBUS_VAR_VALUE_51 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_51
8194 | 2 | MODBUS_VAR_VALUE_52 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_52
8196 | 2 | MODBUS_VAR_VALUE_53 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_53
8198 | 2 | MODBUS_VAR_VALUE_54 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_54
8200 | 2 | MODBUS_VAR_VALUE_55 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_55
8202 | 2 | MODBUS_VAR_VALUE_56 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_56
8204 | 2 | MODBUS_VAR_VALUE_57 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_57
8206 | 2 | MODBUS_VAR_VALUE_58 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_58
8208 | 2 | MODBUS_VAR_VALUE_59 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_59
8210 | 2 | MODBUS_VAR_VALUE_60 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_60
8212 | 2 | MODBUS_VAR_VALUE_61 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_61
8214 | 2 | MODBUS_VAR_VALUE_62 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_62
8216 | 2 | MODBUS_VAR_VALUE_63 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_63
8218 | 2 | MODBUS_VAR_VALUE_64 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_64
8220 | 2 | MODBUS_VAR_VALUE_65 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_65
8222 | 2 | MODBUS_VAR_VALUE_66 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_66
8224 | 2 | MODBUS_VAR_VALUE_67 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_67
8226 | 2 | MODBUS_VAR_VALUE_68 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_68
8228 | 2 | MODBUS_VAR_VALUE_69 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_69
8230 | 2 | MODBUS_VAR_VALUE_70 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_70
8232 | 2 | MODBUS_VAR_VALUE_71 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_71
8234 | 2 | MODBUS_VAR_VALUE_72 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_72
8236 | 2 | MODBUS_VAR_VALUE_73 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_73
8238 | 2 | MODBUS_VAR_VALUE_74 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_74
8240 | 2 | MODBUS_VAR_VALUE_75 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_75
8242 | 2 | MODBUS_VAR_VALUE_76 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_76
8244 | 2 | MODBUS_VAR_VALUE_77 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_77
8246 | 2 | MODBUS_VAR_VALUE_78 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_78
8248 | 2 | MODBUS_VAR_VALUE_79 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_79
8250 | 2 | MODBUS_VAR_VALUE_80 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_80
8252 | 2 | MODBUS_VAR_VALUE_81 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_81
8254 | 2 | MODBUS_VAR_VALUE_82 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_82
8256 | 2 | MODBUS_VAR_VALUE_83 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_83
8258 | 2 | MODBUS_VAR_VALUE_84 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_84
8260 | 2 | MODBUS_VAR_VALUE_85 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_85
8262 | 2 | MODBUS_VAR_VALUE_86 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_86
8264 | 2 | MODBUS_VAR_VALUE_87 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_87
8266 | 2 | MODBUS_VAR_VALUE_88 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_88
8268 | 2 | MODBUS_VAR_VALUE_89 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_89
8270 | 2 | MODBUS_VAR_VALUE_90 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_90
8272 | 2 | MODBUS_VAR_VALUE_91 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_91
8274 | 2 | MODBUS_VAR_VALUE_92 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_92
8276 | 2 | MODBUS_VAR_VALUE_93 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_93
8278 | 2 | MODBUS_VAR_VALUE_94 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_94
8280 | 2 | MODBUS_VAR_VALUE_95 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_95
8282 | 2 | MODBUS_VAR_VALUE_96 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_96
8284 | 2 | MODBUS_VAR_VALUE_97 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_97
8286 | 2 | MODBUS_VAR_VALUE_98 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_98
8288 | 2 | MODBUS_VAR_VALUE_99 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_99
8290 | 2 | MODBUS_VAR_VALUE_100 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_100
8292 | 2 | MODBUS_VAR_VALUE_101 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_101
8294 | 2 | MODBUS_VAR_VALUE_102 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_102
8296 | 2 | MODBUS_VAR_VALUE_103 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_103
8298 | 2 | MODBUS_VAR_VALUE_104 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_104
8300 | 2 | MODBUS_VAR_VALUE_105 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_105
8302 | 2 | MODBUS_VAR_VALUE_106 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_106
8304 | 2 | MODBUS_VAR_VALUE_107 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_107
8306 | 2 | MODBUS_VAR_VALUE_108 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_108
8308 | 2 | MODBUS_VAR_VALUE_109 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_109
8310 | 2 | MODBUS_VAR_VALUE_110 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_110
8312 | 2 | MODBUS_VAR_VALUE_111 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_111
8314 | 2 | MODBUS_VAR_VALUE_112 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_112
8316 | 2 | MODBUS_VAR_VALUE_113 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_113
8318 | 2 | MODBUS_VAR_VALUE_114 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_114
8320 | 2 | MODBUS_VAR_VALUE_115 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_115
8322 | 2 | MODBUS_VAR_VALUE_116 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_116
8324 | 2 | MODBUS_VAR_VALUE_117 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_117
8326 | 2 | MODBUS_VAR_VALUE_118 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_118
8328 | 2 | MODBUS_VAR_VALUE_119 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_119
8330 | 2 | MODBUS_VAR_VALUE_120 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_120
8332 | 2 | MODBUS_VAR_VALUE_121 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_121
8334 | 2 | MODBUS_VAR_VALUE_122 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_122
8336 | 2 | MODBUS_VAR_VALUE_123 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_123
8338 | 2 | MODBUS_VAR_VALUE_124 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_124
8340 | 2 | MODBUS_VAR_VALUE_125 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_125
8342 | 2 | MODBUS_VAR_VALUE_126 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_126
8344 | 2 | MODBUS_VAR_VALUE_127 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_127
8346 | 2 | MODBUS_VAR_VALUE_128 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_128
8348 | 1 | MODBUS_VAR_AM_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Auto or Maunual of variables
8349 | 1 | MODBUS_VAR_AM_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_2
8350 | 1 | MODBUS_VAR_AM_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_3
8351 | 1 | MODBUS_VAR_AM_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_4
8352 | 1 | MODBUS_VAR_AM_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_5
8353 | 1 | MODBUS_VAR_AM_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_6
8354 | 1 | MODBUS_VAR_AM_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_7
8355 | 1 | MODBUS_VAR_AM_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_8
8356 | 1 | MODBUS_VAR_AM_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_9
8357 | 1 | MODBUS_VAR_AM_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_10
8358 | 1 | MODBUS_VAR_AM_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_11
8359 | 1 | MODBUS_VAR_AM_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_12
8360 | 1 | MODBUS_VAR_AM_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_13
8361 | 1 | MODBUS_VAR_AM_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_14
8362 | 1 | MODBUS_VAR_AM_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_15
8363 | 1 | MODBUS_VAR_AM_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_16
8364 | 1 | MODBUS_VAR_AM_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_17
8365 | 1 | MODBUS_VAR_AM_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_18
8366 | 1 | MODBUS_VAR_AM_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_19
8367 | 1 | MODBUS_VAR_AM_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_20
8368 | 1 | MODBUS_VAR_AM_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_21
8369 | 1 | MODBUS_VAR_AM_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_22
8370 | 1 | MODBUS_VAR_AM_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_23
8371 | 1 | MODBUS_VAR_AM_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_24
8372 | 1 | MODBUS_VAR_AM_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_25
8373 | 1 | MODBUS_VAR_AM_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_26
8374 | 1 | MODBUS_VAR_AM_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_27
8375 | 1 | MODBUS_VAR_AM_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_28
8376 | 1 | MODBUS_VAR_AM_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_29
8377 | 1 | MODBUS_VAR_AM_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_30
8378 | 1 | MODBUS_VAR_AM_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_31
8379 | 1 | MODBUS_VAR_AM_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_32
8380 | 1 | MODBUS_VAR_AM_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_33
8381 | 1 | MODBUS_VAR_AM_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_34
8382 | 1 | MODBUS_VAR_AM_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_35
8383 | 1 | MODBUS_VAR_AM_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_36
8384 | 1 | MODBUS_VAR_AM_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_37
8385 | 1 | MODBUS_VAR_AM_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_38
8386 | 1 | MODBUS_VAR_AM_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_39
8387 | 1 | MODBUS_VAR_AM_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_40
8388 | 1 | MODBUS_VAR_AM_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_41
8389 | 1 | MODBUS_VAR_AM_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_42
8390 | 1 | MODBUS_VAR_AM_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_43
8391 | 1 | MODBUS_VAR_AM_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_44
8392 | 1 | MODBUS_VAR_AM_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_45
8393 | 1 | MODBUS_VAR_AM_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_46
8394 | 1 | MODBUS_VAR_AM_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_47
8395 | 1 | MODBUS_VAR_AM_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_48
8396 | 1 | MODBUS_VAR_AM_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_49
8397 | 1 | MODBUS_VAR_AM_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_50
8398 | 1 | MODBUS_VAR_AM_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_51
8399 | 1 | MODBUS_VAR_AM_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_52
8400 | 1 | MODBUS_VAR_AM_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_53
8401 | 1 | MODBUS_VAR_AM_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_54
8402 | 1 | MODBUS_VAR_AM_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_55
8403 | 1 | MODBUS_VAR_AM_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_56
8404 | 1 | MODBUS_VAR_AM_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_57
8405 | 1 | MODBUS_VAR_AM_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_58
8406 | 1 | MODBUS_VAR_AM_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_59
8407 | 1 | MODBUS_VAR_AM_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_60
8408 | 1 | MODBUS_VAR_AM_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_61
8409 | 1 | MODBUS_VAR_AM_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_62
8410 | 1 | MODBUS_VAR_AM_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_63
8411 | 1 | MODBUS_VAR_AM_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_64
8412 | 1 | MODBUS_VAR_AM_65 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_65
8413 | 1 | MODBUS_VAR_AM_66 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_66
8414 | 1 | MODBUS_VAR_AM_67 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_67
8415 | 1 | MODBUS_VAR_AM_68 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_68
8416 | 1 | MODBUS_VAR_AM_69 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_69
8417 | 1 | MODBUS_VAR_AM_70 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_70
8418 | 1 | MODBUS_VAR_AM_71 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_71
8419 | 1 | MODBUS_VAR_AM_72 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_72
8420 | 1 | MODBUS_VAR_AM_73 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_73
8421 | 1 | MODBUS_VAR_AM_74 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_74
8422 | 1 | MODBUS_VAR_AM_75 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_75
8423 | 1 | MODBUS_VAR_AM_76 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_76
8424 | 1 | MODBUS_VAR_AM_77 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_77
8425 | 1 | MODBUS_VAR_AM_78 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_78
8426 | 1 | MODBUS_VAR_AM_79 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_79
8427 | 1 | MODBUS_VAR_AM_80 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_80
8428 | 1 | MODBUS_VAR_AM_81 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_81
8429 | 1 | MODBUS_VAR_AM_82 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_82
8430 | 1 | MODBUS_VAR_AM_83 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_83
8431 | 1 | MODBUS_VAR_AM_84 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_84
8432 | 1 | MODBUS_VAR_AM_85 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_85
8433 | 1 | MODBUS_VAR_AM_86 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_86
8434 | 1 | MODBUS_VAR_AM_87 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_87
8435 | 1 | MODBUS_VAR_AM_88 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_88
8436 | 1 | MODBUS_VAR_AM_89 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_89
8437 | 1 | MODBUS_VAR_AM_90 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_90
8438 | 1 | MODBUS_VAR_AM_91 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_91
8439 | 1 | MODBUS_VAR_AM_92 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_92
8440 | 1 | MODBUS_VAR_AM_93 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_93
8441 | 1 | MODBUS_VAR_AM_94 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_94
8442 | 1 | MODBUS_VAR_AM_95 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_95
8443 | 1 | MODBUS_VAR_AM_96 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_96
8444 | 1 | MODBUS_VAR_AM_97 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_97
8445 | 1 | MODBUS_VAR_AM_98 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_98
8446 | 1 | MODBUS_VAR_AM_99 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_99
8447 | 1 | MODBUS_VAR_AM_100 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_100
8448 | 1 | MODBUS_VAR_AM_101 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_101
8449 | 1 | MODBUS_VAR_AM_102 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_102
8450 | 1 | MODBUS_VAR_AM_103 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_103
8451 | 1 | MODBUS_VAR_AM_104 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_104
8452 | 1 | MODBUS_VAR_AM_105 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_105
8453 | 1 | MODBUS_VAR_AM_106 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_106
8454 | 1 | MODBUS_VAR_AM_107 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_107
8455 | 1 | MODBUS_VAR_AM_108 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_108
8456 | 1 | MODBUS_VAR_AM_109 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_109
8457 | 1 | MODBUS_VAR_AM_110 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_110
8458 | 1 | MODBUS_VAR_AM_111 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_111
8459 | 1 | MODBUS_VAR_AM_112 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_112
8460 | 1 | MODBUS_VAR_AM_113 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_113
8461 | 1 | MODBUS_VAR_AM_114 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_114
8462 | 1 | MODBUS_VAR_AM_115 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_115
8463 | 1 | MODBUS_VAR_AM_116 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_116
8464 | 1 | MODBUS_VAR_AM_117 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_117
8465 | 1 | MODBUS_VAR_AM_118 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_118
8466 | 1 | MODBUS_VAR_AM_119 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_119
8467 | 1 | MODBUS_VAR_AM_120 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_120
8468 | 1 | MODBUS_VAR_AM_121 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_121
8469 | 1 | MODBUS_VAR_AM_122 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_122
8470 | 1 | MODBUS_VAR_AM_123 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_123
8471 | 1 | MODBUS_VAR_AM_124 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_124
8472 | 1 | MODBUS_VAR_AM_125 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_125
8473 | 1 | MODBUS_VAR_AM_126 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_126
8474 | 1 | MODBUS_VAR_AM_127 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_127
8475 | 1 | MODBUS_VAR_AM_128 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_128
8476 | 1 | MODBUS_WEEKLYRROUTINE_AM_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | A/M of weekly_roution (0 - auto, 1- manual)
8477 | 1 | MODBUS_WEEKLYRROUTINE_AM_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_2
8478 | 1 | MODBUS_WEEKLYRROUTINE_AM_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_3
8479 | 1 | MODBUS_WEEKLYRROUTINE_AM_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_4
8480 | 1 | MODBUS_WEEKLYRROUTINE_AM_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_5
8481 | 1 | MODBUS_WEEKLYRROUTINE_AM_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_6
8482 | 1 | MODBUS_WEEKLYRROUTINE_AM_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_7
8483 | 1 | MODBUS_WEEKLYRROUTINE_AM_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_8
8484 | 1 | MODBUS_WR_OUT_VALUE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | value of weekly roution
8485 | 1 | MODBUS_WR_OUT_VALUE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_2
8486 | 1 | MODBUS_WR_OUT_VALUE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_3
8487 | 1 | MODBUS_WR_OUT_VALUE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_4
8488 | 1 | MODBUS_WR_OUT_VALUE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_5
8489 | 1 | MODBUS_WR_OUT_VALUE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_6
8490 | 1 | MODBUS_WR_OUT_VALUE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_7
8491 | 1 | MODBUS_WR_OUT_VALUE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_8
8492 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Holiday1 of weekly roution
8493 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_2
8494 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_3
8495 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_4
8496 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_5
8497 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_6
8498 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_7
8499 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_8
8500 | 1 | MODBUS_WR_STATE1_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | holiday1 state of weekly roution
8501 | 1 | MODBUS_WR_STATE1_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_2
8502 | 1 | MODBUS_WR_STATE1_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_3
8503 | 1 | MODBUS_WR_STATE1_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_4
8504 | 1 | MODBUS_WR_STATE1_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_5
8505 | 1 | MODBUS_WR_STATE1_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_6
8506 | 1 | MODBUS_WR_STATE1_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_7
8507 | 1 | MODBUS_WR_STATE1_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_8
8508 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | holiday2 of weekly roution
8509 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_2
8510 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_3
8511 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_4
8512 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_5
8513 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_6
8514 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_7
8515 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_8
8516 | 1 | MODBUS_WR_STATE2_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | holiday2 state of weekly roution
8517 | 1 | MODBUS_WR_STATE2_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_2
8518 | 1 | MODBUS_WR_STATE2_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_3
8519 | 1 | MODBUS_WR_STATE2_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_4
8520 | 1 | MODBUS_WR_STATE2_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_5
8521 | 1 | MODBUS_WR_STATE2_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_6
8522 | 1 | MODBUS_WR_STATE2_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_7
8523 | 1 | MODBUS_WR_STATE2_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_8
8524 | 1 | MODBUS_AR_AM_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | A/M of Aunnal_roution (0 - auto, 1- manual)
8525 | 1 | MODBUS_AR_AM_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_AM_2
8526 | 1 | MODBUS_AR_AM_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_AM_3
8527 | 1 | MODBUS_AR_AM_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_AM_4
8528 | 1 | MODBUS_AR_OUT_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | value of Aunnal roution
8529 | 1 | MODBUS_AR_OUT_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_OUT_2
8530 | 1 | MODBUS_AR_OUT_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_OUT_3
8531 | 1 | MODBUS_AR_OUT_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_OUT_4
8532 | 1 | MODBUS_VAR_RANGE1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | if it is analog{ unused = 0, degC, degF, FPM, Pa, KPa, psi, in_w, Watts, KW, KWH, Volts, KV, Amps, ma, CFM, Sec, Min, Hours, Days, time_unit, ohms, procent, RH, ppm, counts, Open, CFH, GPM, GPH, GAL, CF, BTU, CMH, custom1, custom2, custom3, custom4, custom5, custom6, custom7, custom8 } if it is digital{ UNUSED = 0, OFF_ON, CLOSED_OPEN, STOP_START, DISABLED_ENABLED, NORMAL_ALARM, NORMAL_HIGH, NORMAL_LOW, NO_YES, COOL_HEAT, UNOCCUPIED_OCCUPIED, LOW_HIGH, ON_OFF , OPEN_CLOSED, START_STOP, ENABLED_DISABLED, ALARM_NORMAL, HIGH_NORMAL, LOW_NORMAL, YES_NO, HEAT_COOL, OCCUPIED_UNOCCUPIED, HIGH_LOW, custom_digital1, custom_digital2, custom_digital3, custom_digital4, custom_digital5, custom_digital6, custom_digital7, custom_digital8 }
8533 | 1 | MODBUS_VAR_RANGE2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8534 | 1 | MODBUS_VAR_RANGE3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8535 | 1 | MODBUS_VAR_RANGE4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8536 | 1 | MODBUS_VAR_RANGE5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8537 | 1 | MODBUS_VAR_RANGE6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8538 | 1 | MODBUS_VAR_RANGE7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8539 | 1 | MODBUS_VAR_RANGE8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8540 | 1 | MODBUS_VAR_RANGE9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8541 | 1 | MODBUS_VAR_RANGE10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8542 | 1 | MODBUS_VAR_RANGE11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8543 | 1 | MODBUS_VAR_RANGE12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8544 | 1 | MODBUS_VAR_RANGE13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8545 | 1 | MODBUS_VAR_RANGE14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8546 | 1 | MODBUS_VAR_RANGE15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8547 | 1 | MODBUS_VAR_RANGE16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8548 | 1 | MODBUS_VAR_RANGE17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8549 | 1 | MODBUS_VAR_RANGE18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8550 | 1 | MODBUS_VAR_RANGE19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8551 | 1 | MODBUS_VAR_RANGE20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8552 | 1 | MODBUS_VAR_RANGE21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8553 | 1 | MODBUS_VAR_RANGE22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8554 | 1 | MODBUS_VAR_RANGE23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8555 | 1 | MODBUS_VAR_RANGE24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8556 | 1 | MODBUS_VAR_RANGE25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8557 | 1 | MODBUS_VAR_RANGE26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8558 | 1 | MODBUS_VAR_RANGE27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8559 | 1 | MODBUS_VAR_RANGE28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8560 | 1 | MODBUS_VAR_RANGE29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8561 | 1 | MODBUS_VAR_RANGE30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8562 | 1 | MODBUS_VAR_RANGE31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8563 | 1 | MODBUS_VAR_RANGE32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8564 | 1 | MODBUS_VAR_RANGE33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8565 | 1 | MODBUS_VAR_RANGE34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8566 | 1 | MODBUS_VAR_RANGE35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8567 | 1 | MODBUS_VAR_RANGE36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8568 | 1 | MODBUS_VAR_RANGE37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8569 | 1 | MODBUS_VAR_RANGE38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8570 | 1 | MODBUS_VAR_RANGE39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8571 | 1 | MODBUS_VAR_RANGE40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8572 | 1 | MODBUS_VAR_RANGE41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8573 | 1 | MODBUS_VAR_RANGE42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8574 | 1 | MODBUS_VAR_RANGE43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8575 | 1 | MODBUS_VAR_RANGE44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8576 | 1 | MODBUS_VAR_RANGE45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8577 | 1 | MODBUS_VAR_RANGE46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8578 | 1 | MODBUS_VAR_RANGE47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8579 | 1 | MODBUS_VAR_RANGE48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8580 | 1 | MODBUS_VAR_RANGE49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8581 | 1 | MODBUS_VAR_RANGE50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8582 | 1 | MODBUS_VAR_RANGE51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8583 | 1 | MODBUS_VAR_RANGE52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8584 | 1 | MODBUS_VAR_RANGE53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8585 | 1 | MODBUS_VAR_RANGE54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8586 | 1 | MODBUS_VAR_RANGE55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8587 | 1 | MODBUS_VAR_RANGE56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8588 | 1 | MODBUS_VAR_RANGE57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8589 | 1 | MODBUS_VAR_RANGE58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8590 | 1 | MODBUS_VAR_RANGE59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8591 | 1 | MODBUS_VAR_RANGE60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8592 | 1 | MODBUS_VAR_RANGE61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8593 | 1 | MODBUS_VAR_RANGE62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8594 | 1 | MODBUS_VAR_RANGE63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8595 | 1 | MODBUS_VAR_RANGE64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8596 | 1 | MODBUS_VAR_RANGE65 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8597 | 1 | MODBUS_VAR_RANGE66 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8598 | 1 | MODBUS_VAR_RANGE67 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8599 | 1 | MODBUS_VAR_RANGE68 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8600 | 1 | MODBUS_VAR_RANGE69 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8601 | 1 | MODBUS_VAR_RANGE70 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8602 | 1 | MODBUS_VAR_RANGE71 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8603 | 1 | MODBUS_VAR_RANGE72 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8604 | 1 | MODBUS_VAR_RANGE73 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8605 | 1 | MODBUS_VAR_RANGE74 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8606 | 1 | MODBUS_VAR_RANGE75 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8607 | 1 | MODBUS_VAR_RANGE76 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8608 | 1 | MODBUS_VAR_RANGE77 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8609 | 1 | MODBUS_VAR_RANGE78 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8610 | 1 | MODBUS_VAR_RANGE79 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8611 | 1 | MODBUS_VAR_RANGE80 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8612 | 1 | MODBUS_VAR_RANGE81 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8613 | 1 | MODBUS_VAR_RANGE82 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8614 | 1 | MODBUS_VAR_RANGE83 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8615 | 1 | MODBUS_VAR_RANGE84 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8616 | 1 | MODBUS_VAR_RANGE85 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8617 | 1 | MODBUS_VAR_RANGE86 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8618 | 1 | MODBUS_VAR_RANGE87 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8619 | 1 | MODBUS_VAR_RANGE88 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8620 | 1 | MODBUS_VAR_RANGE89 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8621 | 1 | MODBUS_VAR_RANGE90 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8622 | 1 | MODBUS_VAR_RANGE91 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8623 | 1 | MODBUS_VAR_RANGE92 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8624 | 1 | MODBUS_VAR_RANGE93 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8625 | 1 | MODBUS_VAR_RANGE94 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8626 | 1 | MODBUS_VAR_RANGE95 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8627 | 1 | MODBUS_VAR_RANGE96 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8628 | 1 | MODBUS_VAR_RANGE97 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8629 | 1 | MODBUS_VAR_RANGE98 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8630 | 1 | MODBUS_VAR_RANGE99 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8631 | 1 | MODBUS_VAR_RANGE100 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8632 | 1 | MODBUS_VAR_RANGE101 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8633 | 1 | MODBUS_VAR_RANGE102 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8634 | 1 | MODBUS_VAR_RANGE103 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8635 | 1 | MODBUS_VAR_RANGE104 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8636 | 1 | MODBUS_VAR_RANGE105 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8637 | 1 | MODBUS_VAR_RANGE106 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8638 | 1 | MODBUS_VAR_RANGE107 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8639 | 1 | MODBUS_VAR_RANGE108 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8640 | 1 | MODBUS_VAR_RANGE109 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8641 | 1 | MODBUS_VAR_RANGE110 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8642 | 1 | MODBUS_VAR_RANGE111 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8643 | 1 | MODBUS_VAR_RANGE112 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8644 | 1 | MODBUS_VAR_RANGE113 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8645 | 1 | MODBUS_VAR_RANGE114 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8646 | 1 | MODBUS_VAR_RANGE115 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8647 | 1 | MODBUS_VAR_RANGE116 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8648 | 1 | MODBUS_VAR_RANGE117 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8649 | 1 | MODBUS_VAR_RANGE118 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8650 | 1 | MODBUS_VAR_RANGE119 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8651 | 1 | MODBUS_VAR_RANGE120 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8652 | 1 | MODBUS_VAR_RANGE121 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8653 | 1 | MODBUS_VAR_RANGE122 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8654 | 1 | MODBUS_VAR_RANGE123 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8655 | 1 | MODBUS_VAR_RANGE124 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8656 | 1 | MODBUS_VAR_RANGE125 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8657 | 1 | MODBUS_VAR_RANGE126 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8658 | 1 | MODBUS_VAR_RANGE127 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8659 | 1 | MODBUS_VAR_RANGE128 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8660 | 1 | MODBUS_VAR_DIGITAL_ANALOG1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8661 | 1 | MODBUS_VAR_DIGITAL_ANALOG2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8662 | 1 | MODBUS_VAR_DIGITAL_ANALOG3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8663 | 1 | MODBUS_VAR_DIGITAL_ANALOG4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8664 | 1 | MODBUS_VAR_DIGITAL_ANALOG5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8665 | 1 | MODBUS_VAR_DIGITAL_ANALOG6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8666 | 1 | MODBUS_VAR_DIGITAL_ANALOG7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8667 | 1 | MODBUS_VAR_DIGITAL_ANALOG8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8668 | 1 | MODBUS_VAR_DIGITAL_ANALOG9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8669 | 1 | MODBUS_VAR_DIGITAL_ANALOG10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8670 | 1 | MODBUS_VAR_DIGITAL_ANALOG11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8671 | 1 | MODBUS_VAR_DIGITAL_ANALOG12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8672 | 1 | MODBUS_VAR_DIGITAL_ANALOG13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8673 | 1 | MODBUS_VAR_DIGITAL_ANALOG14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8674 | 1 | MODBUS_VAR_DIGITAL_ANALOG15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8675 | 1 | MODBUS_VAR_DIGITAL_ANALOG16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8676 | 1 | MODBUS_VAR_DIGITAL_ANALOG17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8677 | 1 | MODBUS_VAR_DIGITAL_ANALOG18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8678 | 1 | MODBUS_VAR_DIGITAL_ANALOG19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8679 | 1 | MODBUS_VAR_DIGITAL_ANALOG20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8680 | 1 | MODBUS_VAR_DIGITAL_ANALOG21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8681 | 1 | MODBUS_VAR_DIGITAL_ANALOG22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8682 | 1 | MODBUS_VAR_DIGITAL_ANALOG23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8683 | 1 | MODBUS_VAR_DIGITAL_ANALOG24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8684 | 1 | MODBUS_VAR_DIGITAL_ANALOG25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8685 | 1 | MODBUS_VAR_DIGITAL_ANALOG26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8686 | 1 | MODBUS_VAR_DIGITAL_ANALOG27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8687 | 1 | MODBUS_VAR_DIGITAL_ANALOG28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8688 | 1 | MODBUS_VAR_DIGITAL_ANALOG29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8689 | 1 | MODBUS_VAR_DIGITAL_ANALOG30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8690 | 1 | MODBUS_VAR_DIGITAL_ANALOG31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8691 | 1 | MODBUS_VAR_DIGITAL_ANALOG32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8692 | 1 | MODBUS_VAR_DIGITAL_ANALOG33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8693 | 1 | MODBUS_VAR_DIGITAL_ANALOG34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8694 | 1 | MODBUS_VAR_DIGITAL_ANALOG35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8695 | 1 | MODBUS_VAR_DIGITAL_ANALOG36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8696 | 1 | MODBUS_VAR_DIGITAL_ANALOG37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8697 | 1 | MODBUS_VAR_DIGITAL_ANALOG38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8698 | 1 | MODBUS_VAR_DIGITAL_ANALOG39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8699 | 1 | MODBUS_VAR_DIGITAL_ANALOG40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8700 | 1 | MODBUS_VAR_DIGITAL_ANALOG41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8701 | 1 | MODBUS_VAR_DIGITAL_ANALOG42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8702 | 1 | MODBUS_VAR_DIGITAL_ANALOG43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8703 | 1 | MODBUS_VAR_DIGITAL_ANALOG44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8704 | 1 | MODBUS_VAR_DIGITAL_ANALOG45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8705 | 1 | MODBUS_VAR_DIGITAL_ANALOG46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8706 | 1 | MODBUS_VAR_DIGITAL_ANALOG47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8707 | 1 | MODBUS_VAR_DIGITAL_ANALOG48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8708 | 1 | MODBUS_VAR_DIGITAL_ANALOG49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8709 | 1 | MODBUS_VAR_DIGITAL_ANALOG50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8710 | 1 | MODBUS_VAR_DIGITAL_ANALOG51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8711 | 1 | MODBUS_VAR_DIGITAL_ANALOG52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8712 | 1 | MODBUS_VAR_DIGITAL_ANALOG53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8713 | 1 | MODBUS_VAR_DIGITAL_ANALOG54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8714 | 1 | MODBUS_VAR_DIGITAL_ANALOG55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8715 | 1 | MODBUS_VAR_DIGITAL_ANALOG56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8716 | 1 | MODBUS_VAR_DIGITAL_ANALOG57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8717 | 1 | MODBUS_VAR_DIGITAL_ANALOG58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8718 | 1 | MODBUS_VAR_DIGITAL_ANALOG59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8719 | 1 | MODBUS_VAR_DIGITAL_ANALOG60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8720 | 1 | MODBUS_VAR_DIGITAL_ANALOG61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8721 | 1 | MODBUS_VAR_DIGITAL_ANALOG62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8722 | 1 | MODBUS_VAR_DIGITAL_ANALOG63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8723 | 1 | MODBUS_VAR_DIGITAL_ANALOG64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8724 | 1 | MODBUS_VAR_DIGITAL_ANALOG65 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8725 | 1 | MODBUS_VAR_DIGITAL_ANALOG66 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8726 | 1 | MODBUS_VAR_DIGITAL_ANALOG67 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8727 | 1 | MODBUS_VAR_DIGITAL_ANALOG68 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8728 | 1 | MODBUS_VAR_DIGITAL_ANALOG69 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8729 | 1 | MODBUS_VAR_DIGITAL_ANALOG70 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8730 | 1 | MODBUS_VAR_DIGITAL_ANALOG71 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8731 | 1 | MODBUS_VAR_DIGITAL_ANALOG72 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8732 | 1 | MODBUS_VAR_DIGITAL_ANALOG73 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8733 | 1 | MODBUS_VAR_DIGITAL_ANALOG74 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8734 | 1 | MODBUS_VAR_DIGITAL_ANALOG75 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8735 | 1 | MODBUS_VAR_DIGITAL_ANALOG76 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8736 | 1 | MODBUS_VAR_DIGITAL_ANALOG77 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8737 | 1 | MODBUS_VAR_DIGITAL_ANALOG78 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8738 | 1 | MODBUS_VAR_DIGITAL_ANALOG79 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8739 | 1 | MODBUS_VAR_DIGITAL_ANALOG80 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8740 | 1 | MODBUS_VAR_DIGITAL_ANALOG81 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8741 | 1 | MODBUS_VAR_DIGITAL_ANALOG82 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8742 | 1 | MODBUS_VAR_DIGITAL_ANALOG83 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8743 | 1 | MODBUS_VAR_DIGITAL_ANALOG84 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8744 | 1 | MODBUS_VAR_DIGITAL_ANALOG85 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8745 | 1 | MODBUS_VAR_DIGITAL_ANALOG86 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8746 | 1 | MODBUS_VAR_DIGITAL_ANALOG87 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8747 | 1 | MODBUS_VAR_DIGITAL_ANALOG88 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8748 | 1 | MODBUS_VAR_DIGITAL_ANALOG89 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8749 | 1 | MODBUS_VAR_DIGITAL_ANALOG90 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8750 | 1 | MODBUS_VAR_DIGITAL_ANALOG91 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8751 | 1 | MODBUS_VAR_DIGITAL_ANALOG92 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8752 | 1 | MODBUS_VAR_DIGITAL_ANALOG93 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8753 | 1 | MODBUS_VAR_DIGITAL_ANALOG94 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8754 | 1 | MODBUS_VAR_DIGITAL_ANALOG95 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8755 | 1 | MODBUS_VAR_DIGITAL_ANALOG96 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8756 | 1 | MODBUS_VAR_DIGITAL_ANALOG97 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8757 | 1 | MODBUS_VAR_DIGITAL_ANALOG98 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8758 | 1 | MODBUS_VAR_DIGITAL_ANALOG99 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8759 | 1 | MODBUS_VAR_DIGITAL_ANALOG100 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8760 | 1 | MODBUS_VAR_DIGITAL_ANALOG101 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8761 | 1 | MODBUS_VAR_DIGITAL_ANALOG102 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8762 | 1 | MODBUS_VAR_DIGITAL_ANALOG103 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8763 | 1 | MODBUS_VAR_DIGITAL_ANALOG104 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8764 | 1 | MODBUS_VAR_DIGITAL_ANALOG105 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8765 | 1 | MODBUS_VAR_DIGITAL_ANALOG106 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8766 | 1 | MODBUS_VAR_DIGITAL_ANALOG107 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8767 | 1 | MODBUS_VAR_DIGITAL_ANALOG108 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8768 | 1 | MODBUS_VAR_DIGITAL_ANALOG109 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8769 | 1 | MODBUS_VAR_DIGITAL_ANALOG110 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8770 | 1 | MODBUS_VAR_DIGITAL_ANALOG111 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8771 | 1 | MODBUS_VAR_DIGITAL_ANALOG112 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8772 | 1 | MODBUS_VAR_DIGITAL_ANALOG113 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8773 | 1 | MODBUS_VAR_DIGITAL_ANALOG114 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8774 | 1 | MODBUS_VAR_DIGITAL_ANALOG115 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8775 | 1 | MODBUS_VAR_DIGITAL_ANALOG116 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8776 | 1 | MODBUS_VAR_DIGITAL_ANALOG117 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8777 | 1 | MODBUS_VAR_DIGITAL_ANALOG118 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8778 | 1 | MODBUS_VAR_DIGITAL_ANALOG119 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8779 | 1 | MODBUS_VAR_DIGITAL_ANALOG120 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8780 | 1 | MODBUS_VAR_DIGITAL_ANALOG121 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8781 | 1 | MODBUS_VAR_DIGITAL_ANALOG122 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8782 | 1 | MODBUS_VAR_DIGITAL_ANALOG123 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8783 | 1 | MODBUS_VAR_DIGITAL_ANALOG124 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8784 | 1 | MODBUS_VAR_DIGITAL_ANALOG125 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8785 | 1 | MODBUS_VAR_DIGITAL_ANALOG126 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8786 | 1 | MODBUS_VAR_DIGITAL_ANALOG127 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8787 | 1 | MODBUS_VAR_DIGITAL_ANALOG128 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
15808 | 21 | MODBUS_SCHEDULE_LIST1 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | 15808 - 15817 Full Lable 21 characters 10.5 registers 15818 - 15822 Lable 9 characters 4.5 registers 15823 High Byte-> Output(ON/OFF) Low Byte-> Auto/Manual 15824 High Byte-> Holiday1(ON/OFF) Low Byte-> Holiday2(ON/OFF) 15825 unused 15826 3bytes (That tells you which Holiday to fill in)
15829 | 21 | MODBUS_SCHEDULE_LIST2 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15850 | 21 | MODBUS_SCHEDULE_LIST3 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15871 | 21 | MODBUS_SCHEDULE_LIST4 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15892 | 21 | MODBUS_SCHEDULE_LIST5 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15913 | 21 | MODBUS_SCHEDULE_LIST6 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15934 | 21 | MODBUS_SCHEDULE_LIST7 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15955 | 21 | MODBUS_SCHEDULE_LIST8 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
32044 | 72 | MODBUS_SCHEDULE_LIST1_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday example: Monday 32044 - 32051 8 registers ON_1 32044 e.g. Value is 0x0607 Means 07:06 OFF_1 32045 e.g. Value is 0x1110 Means 16:17 ON_2 32046 OFF_2 32047 ON_3 32048 OFF_3 32049 ON_4 32050 OFF_4 32051 The rest is the same as Monday TuesDay 32052 - 32059 Wednesday 32060 - 32067 Thursday 32068 - 32075 Friday 32076 - 32083 Suturday 32084 - 32091 Sunday 32092 - 32099 Holiday1 32100 - 32107 Holiday2 32108 - 32115
32116 | 72 | MODBUS_SCHEDULE_LIST2_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32116 … Same as above mentioned
32188 | 72 | MODBUS_SCHEDULE_LIST3_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32188 Same as above mentioned
32260 | 72 | MODBUS_SCHEDULE_LIST4_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32260 Same as above mentioned
32332 | 72 | MODBUS_SCHEDULE_LIST5_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32332 Same as above mentioned
32404 | 72 | MODBUS_SCHEDULE_LIST6_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32404 Same as above mentioned
32476 | 72 | MODBUS_SCHEDULE_LIST7_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32476 Same as above mentioned
32548 | 72 | MODBUS_SCHEDULE_LIST8_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32548 Same as above mentioned
33201 | 36 | MODBUS_SCHEDULE_FLAG1 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | example: Hi byte -- FLAG of Event1,Event3,Event5,Event7 Low byte -- Flag of Event2,Eevet4,Event6,Event8 1: ON 0:OFF 0xff:unused
33237 | 36 | MODBUS_SCHEDULE_FLAG2 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33273 | 36 | MODBUS_SCHEDULE_FLAG3 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33309 | 36 | MODBUS_SCHEDULE_FLAG4 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33345 | 36 | MODBUS_SCHEDULE_FLAG5 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33381 | 36 | MODBUS_SCHEDULE_FLAG6 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33417 | 36 | MODBUS_SCHEDULE_FLAG7 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33453 | 36 | MODBUS_SCHEDULE_FLAG8 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned

## T3_XB_ESP
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 1 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version Low
5 | 1 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version High
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model = 88
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
12 | 1 | MODBUS_UART0_BAUDRATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Baudrate of sub port.(UART_1200 = 0, UART_2400 = 1, UART_3600 = 2, UART_4800 = 3, UART_7200 = 4, UART_9600 = 5, UART_19200 = 6, UART_38400 = 7, UART_76800 = 8, UART_115200 = 9, UART_921600 = 10, UART_57600 = 11
14 | 1 | MODBUS_ISP_VER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | ISP Version
18 | 1 | MODBUS_UART2_BAUDRATE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Baudrate of main port.(UART_1200 = 0, UART_2400 = 1, UART_3600 = 2, UART_4800 = 3, UART_7200 = 4, UART_9600 = 5, UART_19200 = 6, UART_38400 = 7, UART_76800 = 8, UART_115200 = 9, UART_921600 = 10, UART_57600 = 11
19 | 1 | MODBUS_COM0_TYPE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | SUB port configure NOUSE = 0, BACNET_SLAVE = 1, MODBUS_SLAVE = 2, MODBUS_MASTER = 7, BACNET_MASTER = 9
21 | 1 | MODBUS_COM2_TYPE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | main port configure NOUSE = 0, BACNET_SLAVE = 1, MODBUS_SLAVE = 2, MODBUS_MASTER = 7, BACNET_MASTER = 9
32 | 1 | MODBUS_INSTANCE_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | High word of instance number
33 | 1 | MODBUS_RESET | 06 Write Single Register | 16 Bit Unsigned Integer | write 111 to reset
34 | 1 | MODBUS_MINI_TYPE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Board type, big or small. 1 - big , 2 - samll,3-tiny,4-vav
35 | 1 | MODBUS_INSTANCE_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Low word of instance number
36 | 1 | MODBUS_PANEL_NUMBER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Panel number
42 | 1 | MODBUS_STATION_NUM | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Station NUM of mstp commucnication
46 | 1 | MODBUS_NETWORK_NUMBER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | NETWORK_NUMBER
47 | 1 | MODBUS_MSTP_NETWORK | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | MSTP NETWORK
60 | 1 | MODBUS_MAC_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC address_1
61 | 1 | MODBUS_MAC_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC address_2
62 | 1 | MODBUS_MAC_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC address_3
63 | 1 | MODBUS_MAC_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC address_4
64 | 1 | MODBUS_MAC_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC address_5
65 | 1 | MODBUS_MAC_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC address_6
66 | 1 | MODBUS_TCP_TYPE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | IP mode. 0=static IP; 1= DHCP
67 | 1 | MODBUS_IP_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address_1
68 | 1 | MODBUS_IP_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address_2
69 | 1 | MODBUS_IP_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address_3
70 | 1 | MODBUS_IP_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address_4
71 | 1 | MODBUS_SUBNET_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | subnet_1
72 | 1 | MODBUS_SUBNET_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | subnet_2
73 | 1 | MODBUS_SUBNET_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | subnet_3
74 | 1 | MODBUS_SUBNET_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | subnet_4
75 | 1 | MODBUS_GETWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | getway_1
76 | 1 | MODBUS_GETWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | getway_2
77 | 1 | MODBUS_GETWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | getway_3
78 | 1 | MODBUS_GETWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | getway_4
80 | 1 | WIFI_RSSI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | RSSI of wifi
81 | 1 | MODBUS_TCP_LISTEN_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | listen port at TCP server mode
85 | 2 | MODBUS_READ_POINT_TIMER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Interval for reading the point of the sub-device
94 | 2 | MODBUS_RUN_TIME | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | run time,94 is low word, 95 is high word.
98 | 1 | MODBUS_LCD_TIME_OFF_DELAY | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | For TSTAT10, 0 - BACKLIGHT OFF, 255-BACKLIGHT ON, other - delay time
200 | 1 | MODBUS_TIMER_SYNC_SECOND | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:second
201 | 1 | MODBUS_TIMER_SYNC_MIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync: min
202 | 1 | MODBUS_TIMER_SYNC_HOUR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:hour
203 | 1 | MODBUS_TIMER_SYNC_DAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:day
204 | 1 | MODBUS_TIMER_SYNC_DAY_OF_WEEK | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:day of week
205 | 1 | MODBUS_TIMER_SYNC_MONTH | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:month
206 | 1 | MODBUS_TIMER_SYNC_YEAR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Last Time Sync:year
299 | 1 | MODBUS_TOTAL_NO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Number of tstat
300 | 1 | MODBUS_SUBADDR_FIRST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | id of sub tstat ,from 300 to 400
500 | 2 | MODBUS_NG2_TEMP1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | temperature of 1st SHT4X(only for NG2)
501 | 2 | MODBUS_NG2_HUM1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | humdity of 1st SHT4X(only for NG2)
502 | 2 | MODBUS_NG2_TEMP2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | temperature of 2nd SHT4X(only for NG2)
503 | 2 | MODBUS_NG2_HUM2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | humdity of 2nd SHT4X(only for NG2)
504 | 2 | MODBUS_NG2_TEMP3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | temperature of 3rd SHT4X(only for NG2)
505 | 2 | MODBUS_NG2_HUM3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | humdity of 3rd SHT4X(only for NG2)
728 | 1 | MODBUS_TSTAT10_ICON_CONFIG | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Icon config of tstat10
729 | 1 | MODBUS_DISALBE_TSTAT10_DIS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | display icons and scrolling string, 0 - default show icon and scrolling string, 1 - disable both , 2 - show scrolling, no icon
730 | 1 | MODBUS_TSTAT10_TEMPERATURE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | temperature of tstat10
731 | 1 | MODBUS_TSTAT10_TVOC | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | tvoc of tstat10
732 | 1 | MODBUS_TSTAT10_HUMIDITY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | humidity of tstat10
733 | 1 | MODBUS_TSTAT10_OCCUPIED | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | occupide status of tstat10
734 | 1 | MODBUS_TSTAT10_CO2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | co2 of tstat10
735 | 1 | MODBUS_TSTAT10_LIGHT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | light of tstat10
736 | 1 | MODBUS_TSTAT10_VOICE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | voice of tstat10
740 | 1 | MODBUS_TSTAT10_PULSE1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | pulse count1 of tstat10
741 | 1 | MODBUS_TSTAT10_PULSE2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | pulse count2 of tstat10
742 | 1 | MODBUS_TSTAT10_PULSE3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | pulse count3 of tstat10
743 | 1 | MODBUS_TSTAT10_PULSE4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | pulse count4 of tstat10
744 | 1 | MODBUS_TSTAT10_CO2_CALIBRATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | calibration value of CO2
745 | 1 | MODBUS_TSTAT10_HUM_DEW_PT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | DEW point of HUM, uint is C
746 | 1 | MODBUS_TSTAT10_HUM_DEW_PT_F | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | DEW point of HUM, uint is F
747 | 1 | MODBUS_TSTAT10_HUM_PWS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | HumSensor_Pws
748 | 1 | MODBUS_TSTAT10_HUM_MIX_RADIO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | HumSensor_Mix_Ratio
749 | 1 | MODBUS_TSTAT10_HUM_ENTHALPY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | HumSensor_Enthalpy
2000 | 1 | MODBUS_WIFI_SSID_MANUAL_EN | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Enable wifi. 0 - default, 1 - Enable, 2 - disable
2001 | 1 | MODBUS_WIFI_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI IP MODE , 0-DHCP,1-STATIC
2004 | 1 | MODBUS_WIFI_MODBUS_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WIFI_MODBUS_PORT ,Default value :502
2005 | 1 | MODBUS_WIFI_BACNET_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | BACnet PORT , Default value :47808
2010 | 32 | MODBUS_WIFI_SSID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | WIFI_SSID
2042 | 16 | MODBUS_WIFI_PASSWORD | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | WIFI_PASSWORD
2058 | 1 | MODBUS_WIFI_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_IP_ADDRESS_1
2059 | 1 | MODBUS_WIFI_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_IP_ADDRESS_2
2060 | 1 | MODBUS_WIFI_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_IP_ADDRESS_3
2061 | 1 | MODBUS_WIFI_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_IP_ADDRESS_4
2062 | 1 | MODBUS_WIFI_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_SUBNET_MASK_1
2063 | 1 | MODBUS_WIFI_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_SUBNET_MASK_2
2064 | 1 | MODBUS_WIFI_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_SUBNET_MASK_3
2065 | 1 | MODBUS_WIFI_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_SUBNET_MASK_4
2066 | 1 | MODBUS_WIFI_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_GATEWAY_1
2067 | 1 | MODBUS_WIFI_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_GATEWAY_2
2068 | 1 | MODBUS_WIFI_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_GATEWAY_3
2069 | 1 | MODBUS_WIFI_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI_GATEWAY_4
2070 | 1 | MODBUS_WIFI_MAC_ADDRESS_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_1
2071 | 1 | MODBUS_WIFI_MAC_ADDRESS_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_2
2072 | 1 | MODBUS_WIFI_MAC_ADDRESS_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_3
2073 | 1 | MODBUS_WIFI_MAC_ADDRESS_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_4
2074 | 1 | MODBUS_WIFI_MAC_ADDRESS_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_5
2075 | 1 | MODBUS_WIFI_MAC_ADDRESS_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | WIFI_MAC_ADDRESS_6
7100 | 2 | MODBUS_OUTPUT_VALUE_1 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | eg:high register 7100 . Low register 7101 Value = high_register*65536 + low_register If value is 12345 , all this value divide 1000 . calculate to three decimal places , that means 12.345
7102 | 2 | MODBUS_OUTPUT_VALUE_2 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_2
7104 | 2 | MODBUS_OUTPUT_VALUE_3 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_3
7106 | 2 | MODBUS_OUTPUT_VALUE_4 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_4
7108 | 2 | MODBUS_OUTPUT_VALUE_5 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_5
7110 | 2 | MODBUS_OUTPUT_VALUE_6 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_6
7112 | 2 | MODBUS_OUTPUT_VALUE_7 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_7
7114 | 2 | MODBUS_OUTPUT_VALUE_8 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_8
7116 | 2 | MODBUS_OUTPUT_VALUE_9 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_9
7118 | 2 | MODBUS_OUTPUT_VALUE_10 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_10
7120 | 2 | MODBUS_OUTPUT_VALUE_11 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_11
7122 | 2 | MODBUS_OUTPUT_VALUE_12 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_12
7124 | 2 | MODBUS_OUTPUT_VALUE_13 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_13
7126 | 2 | MODBUS_OUTPUT_VALUE_14 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_14
7128 | 2 | MODBUS_OUTPUT_VALUE_15 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_15
7130 | 2 | MODBUS_OUTPUT_VALUE_16 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_16
7132 | 2 | MODBUS_OUTPUT_VALUE_17 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_17
7134 | 2 | MODBUS_OUTPUT_VALUE_18 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_18
7136 | 2 | MODBUS_OUTPUT_VALUE_19 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_19
7138 | 2 | MODBUS_OUTPUT_VALUE_20 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_20
7140 | 2 | MODBUS_OUTPUT_VALUE_21 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_21
7142 | 2 | MODBUS_OUTPUT_VALUE_22 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_22
7144 | 2 | MODBUS_OUTPUT_VALUE_23 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_23
7146 | 2 | MODBUS_OUTPUT_VALUE_24 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_24
7148 | 2 | MODBUS_OUTPUT_VALUE_25 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_25
7150 | 2 | MODBUS_OUTPUT_VALUE_26 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_26
7152 | 2 | MODBUS_OUTPUT_VALUE_27 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_27
7154 | 2 | MODBUS_OUTPUT_VALUE_28 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_28
7156 | 2 | MODBUS_OUTPUT_VALUE_29 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_29
7158 | 2 | MODBUS_OUTPUT_VALUE_30 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_30
7160 | 2 | MODBUS_OUTPUT_VALUE_31 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_31
7162 | 2 | MODBUS_OUTPUT_VALUE_32 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_32
7164 | 2 | MODBUS_OUTPUT_VALUE_33 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_33
7166 | 2 | MODBUS_OUTPUT_VALUE_34 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_34
7168 | 2 | MODBUS_OUTPUT_VALUE_35 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_35
7170 | 2 | MODBUS_OUTPUT_VALUE_36 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_36
7172 | 2 | MODBUS_OUTPUT_VALUE_37 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_37
7174 | 2 | MODBUS_OUTPUT_VALUE_38 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_38
7176 | 2 | MODBUS_OUTPUT_VALUE_39 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_39
7178 | 2 | MODBUS_OUTPUT_VALUE_40 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_40
7180 | 2 | MODBUS_OUTPUT_VALUE_41 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_41
7182 | 2 | MODBUS_OUTPUT_VALUE_42 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_42
7184 | 2 | MODBUS_OUTPUT_VALUE_43 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_43
7186 | 2 | MODBUS_OUTPUT_VALUE_44 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_44
7188 | 2 | MODBUS_OUTPUT_VALUE_45 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_45
7190 | 2 | MODBUS_OUTPUT_VALUE_46 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_46
7192 | 2 | MODBUS_OUTPUT_VALUE_47 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_47
7194 | 2 | MODBUS_OUTPUT_VALUE_48 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_48
7196 | 2 | MODBUS_OUTPUT_VALUE_49 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_49
7198 | 2 | MODBUS_OUTPUT_VALUE_50 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_50
7200 | 2 | MODBUS_OUTPUT_VALUE_51 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_51
7202 | 2 | MODBUS_OUTPUT_VALUE_52 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_52
7204 | 2 | MODBUS_OUTPUT_VALUE_53 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_53
7206 | 2 | MODBUS_OUTPUT_VALUE_54 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_54
7208 | 2 | MODBUS_OUTPUT_VALUE_55 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_55
7210 | 2 | MODBUS_OUTPUT_VALUE_56 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_56
7212 | 2 | MODBUS_OUTPUT_VALUE_57 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_57
7214 | 2 | MODBUS_OUTPUT_VALUE_58 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_58
7216 | 2 | MODBUS_OUTPUT_VALUE_59 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_59
7218 | 2 | MODBUS_OUTPUT_VALUE_60 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_60
7220 | 2 | MODBUS_OUTPUT_VALUE_61 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_61
7222 | 2 | MODBUS_OUTPUT_VALUE_62 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_62
7224 | 2 | MODBUS_OUTPUT_VALUE_63 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_63
7226 | 2 | MODBUS_OUTPUT_VALUE_64 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | OUTPUT_VALUE_64
7228 | 1 | MODBUS_OUTPUT_SWICH_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output swith status (SW_OFF - 0, SW_AUTO - 1, SW_HAND - 2)
7229 | 1 | MODBUS_OUTPUT_SWICH_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_2
7230 | 1 | MODBUS_OUTPUT_SWICH_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_3
7231 | 1 | MODBUS_OUTPUT_SWICH_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_4
7232 | 1 | MODBUS_OUTPUT_SWICH_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_5
7233 | 1 | MODBUS_OUTPUT_SWICH_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_6
7234 | 1 | MODBUS_OUTPUT_SWICH_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_7
7235 | 1 | MODBUS_OUTPUT_SWICH_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_8
7236 | 1 | MODBUS_OUTPUT_SWICH_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_9
7237 | 1 | MODBUS_OUTPUT_SWICH_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_10
7238 | 1 | MODBUS_OUTPUT_SWICH_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_11
7239 | 1 | MODBUS_OUTPUT_SWICH_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_12
7240 | 1 | MODBUS_OUTPUT_SWICH_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_13
7241 | 1 | MODBUS_OUTPUT_SWICH_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_14
7242 | 1 | MODBUS_OUTPUT_SWICH_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_15
7243 | 1 | MODBUS_OUTPUT_SWICH_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_16
7244 | 1 | MODBUS_OUTPUT_SWICH_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_17
7245 | 1 | MODBUS_OUTPUT_SWICH_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_18
7246 | 1 | MODBUS_OUTPUT_SWICH_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_19
7247 | 1 | MODBUS_OUTPUT_SWICH_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_20
7248 | 1 | MODBUS_OUTPUT_SWICH_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_21
7249 | 1 | MODBUS_OUTPUT_SWICH_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_22
7250 | 1 | MODBUS_OUTPUT_SWICH_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_23
7251 | 1 | MODBUS_OUTPUT_SWICH_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_24
7252 | 1 | MODBUS_OUTPUT_SWICH_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_25
7253 | 1 | MODBUS_OUTPUT_SWICH_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_26
7254 | 1 | MODBUS_OUTPUT_SWICH_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_27
7255 | 1 | MODBUS_OUTPUT_SWICH_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_28
7256 | 1 | MODBUS_OUTPUT_SWICH_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_29
7257 | 1 | MODBUS_OUTPUT_SWICH_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_30
7258 | 1 | MODBUS_OUTPUT_SWICH_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_31
7259 | 1 | MODBUS_OUTPUT_SWICH_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_32
7260 | 1 | MODBUS_OUTPUT_SWICH_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_33
7261 | 1 | MODBUS_OUTPUT_SWICH_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_34
7262 | 1 | MODBUS_OUTPUT_SWICH_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_35
7263 | 1 | MODBUS_OUTPUT_SWICH_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_36
7264 | 1 | MODBUS_OUTPUT_SWICH_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_37
7265 | 1 | MODBUS_OUTPUT_SWICH_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_38
7266 | 1 | MODBUS_OUTPUT_SWICH_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_39
7267 | 1 | MODBUS_OUTPUT_SWICH_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_40
7268 | 1 | MODBUS_OUTPUT_SWICH_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_41
7269 | 1 | MODBUS_OUTPUT_SWICH_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_42
7270 | 1 | MODBUS_OUTPUT_SWICH_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_43
7271 | 1 | MODBUS_OUTPUT_SWICH_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_44
7272 | 1 | MODBUS_OUTPUT_SWICH_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_45
7273 | 1 | MODBUS_OUTPUT_SWICH_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_46
7274 | 1 | MODBUS_OUTPUT_SWICH_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_47
7275 | 1 | MODBUS_OUTPUT_SWICH_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_48
7276 | 1 | MODBUS_OUTPUT_SWICH_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_49
7277 | 1 | MODBUS_OUTPUT_SWICH_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_50
7278 | 1 | MODBUS_OUTPUT_SWICH_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_51
7279 | 1 | MODBUS_OUTPUT_SWICH_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_52
7280 | 1 | MODBUS_OUTPUT_SWICH_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_53
7281 | 1 | MODBUS_OUTPUT_SWICH_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_54
7282 | 1 | MODBUS_OUTPUT_SWICH_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_55
7283 | 1 | MODBUS_OUTPUT_SWICH_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_56
7284 | 1 | MODBUS_OUTPUT_SWICH_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_57
7285 | 1 | MODBUS_OUTPUT_SWICH_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_58
7286 | 1 | MODBUS_OUTPUT_SWICH_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_59
7287 | 1 | MODBUS_OUTPUT_SWICH_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_60
7288 | 1 | MODBUS_OUTPUT_SWICH_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_61
7289 | 1 | MODBUS_OUTPUT_SWICH_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_62
7290 | 1 | MODBUS_OUTPUT_SWICH_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_63
7291 | 1 | MODBUS_OUTPUT_SWICH_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_SWICH_64
7292 | 1 | MODBUS_OUTPUT_RANGE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
7293 | 1 | MODBUS_OUTPUT_RANGE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_2
7294 | 1 | MODBUS_OUTPUT_RANGE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_3
7295 | 1 | MODBUS_OUTPUT_RANGE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_4
7296 | 1 | MODBUS_OUTPUT_RANGE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_5
7297 | 1 | MODBUS_OUTPUT_RANGE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_6
7298 | 1 | MODBUS_OUTPUT_RANGE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_7
7299 | 1 | MODBUS_OUTPUT_RANGE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_8
7300 | 1 | MODBUS_OUTPUT_RANGE_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_9
7301 | 1 | MODBUS_OUTPUT_RANGE_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_10
7302 | 1 | MODBUS_OUTPUT_RANGE_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_11
7303 | 1 | MODBUS_OUTPUT_RANGE_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_12
7304 | 1 | MODBUS_OUTPUT_RANGE_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_13
7305 | 1 | MODBUS_OUTPUT_RANGE_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_14
7306 | 1 | MODBUS_OUTPUT_RANGE_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_15
7307 | 1 | MODBUS_OUTPUT_RANGE_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_16
7308 | 1 | MODBUS_OUTPUT_RANGE_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_17
7309 | 1 | MODBUS_OUTPUT_RANGE_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_18
7310 | 1 | MODBUS_OUTPUT_RANGE_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_19
7311 | 1 | MODBUS_OUTPUT_RANGE_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_20
7312 | 1 | MODBUS_OUTPUT_RANGE_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_21
7313 | 1 | MODBUS_OUTPUT_RANGE_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_22
7314 | 1 | MODBUS_OUTPUT_RANGE_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_23
7315 | 1 | MODBUS_OUTPUT_RANGE_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_24
7316 | 1 | MODBUS_OUTPUT_RANGE_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_25
7317 | 1 | MODBUS_OUTPUT_RANGE_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_26
7318 | 1 | MODBUS_OUTPUT_RANGE_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_27
7319 | 1 | MODBUS_OUTPUT_RANGE_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_28
7320 | 1 | MODBUS_OUTPUT_RANGE_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_29
7321 | 1 | MODBUS_OUTPUT_RANGE_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_30
7322 | 1 | MODBUS_OUTPUT_RANGE_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_31
7323 | 1 | MODBUS_OUTPUT_RANGE_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_32
7324 | 1 | MODBUS_OUTPUT_RANGE_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_33
7325 | 1 | MODBUS_OUTPUT_RANGE_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_34
7326 | 1 | MODBUS_OUTPUT_RANGE_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_35
7327 | 1 | MODBUS_OUTPUT_RANGE_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_36
7328 | 1 | MODBUS_OUTPUT_RANGE_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_37
7329 | 1 | MODBUS_OUTPUT_RANGE_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_38
7330 | 1 | MODBUS_OUTPUT_RANGE_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_39
7331 | 1 | MODBUS_OUTPUT_RANGE_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_40
7332 | 1 | MODBUS_OUTPUT_RANGE_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_41
7333 | 1 | MODBUS_OUTPUT_RANGE_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_42
7334 | 1 | MODBUS_OUTPUT_RANGE_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_43
7335 | 1 | MODBUS_OUTPUT_RANGE_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_44
7336 | 1 | MODBUS_OUTPUT_RANGE_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_45
7337 | 1 | MODBUS_OUTPUT_RANGE_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_46
7338 | 1 | MODBUS_OUTPUT_RANGE_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_47
7339 | 1 | MODBUS_OUTPUT_RANGE_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_48
7340 | 1 | MODBUS_OUTPUT_RANGE_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_49
7341 | 1 | MODBUS_OUTPUT_RANGE_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_50
7342 | 1 | MODBUS_OUTPUT_RANGE_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_51
7343 | 1 | MODBUS_OUTPUT_RANGE_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_52
7344 | 1 | MODBUS_OUTPUT_RANGE_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_53
7345 | 1 | MODBUS_OUTPUT_RANGE_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_54
7346 | 1 | MODBUS_OUTPUT_RANGE_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_55
7347 | 1 | MODBUS_OUTPUT_RANGE_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_56
7348 | 1 | MODBUS_OUTPUT_RANGE_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_57
7349 | 1 | MODBUS_OUTPUT_RANGE_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_58
7350 | 1 | MODBUS_OUTPUT_RANGE_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_59
7351 | 1 | MODBUS_OUTPUT_RANGE_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_60
7352 | 1 | MODBUS_OUTPUT_RANGE_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_61
7353 | 1 | MODBUS_OUTPUT_RANGE_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_62
7354 | 1 | MODBUS_OUTPUT_RANGE_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_63
7355 | 1 | MODBUS_OUTPUT_RANGE_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_RANGE_64
7356 | 1 | MODBUS_OUTPUT_AM_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output auto or manual (0 - auto, 1- manual)
7357 | 1 | MODBUS_OUTPUT_AM_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_2
7358 | 1 | MODBUS_OUTPUT_AM_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_3
7359 | 1 | MODBUS_OUTPUT_AM_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_4
7360 | 1 | MODBUS_OUTPUT_AM_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_5
7361 | 1 | MODBUS_OUTPUT_AM_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_6
7362 | 1 | MODBUS_OUTPUT_AM_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_7
7363 | 1 | MODBUS_OUTPUT_AM_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_8
7364 | 1 | MODBUS_OUTPUT_AM_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_9
7365 | 1 | MODBUS_OUTPUT_AM_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_10
7366 | 1 | MODBUS_OUTPUT_AM_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_11
7367 | 1 | MODBUS_OUTPUT_AM_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_12
7368 | 1 | MODBUS_OUTPUT_AM_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_13
7369 | 1 | MODBUS_OUTPUT_AM_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_14
7370 | 1 | MODBUS_OUTPUT_AM_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_15
7371 | 1 | MODBUS_OUTPUT_AM_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_16
7372 | 1 | MODBUS_OUTPUT_AM_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_17
7373 | 1 | MODBUS_OUTPUT_AM_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_18
7374 | 1 | MODBUS_OUTPUT_AM_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_19
7375 | 1 | MODBUS_OUTPUT_AM_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_20
7376 | 1 | MODBUS_OUTPUT_AM_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_21
7377 | 1 | MODBUS_OUTPUT_AM_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_22
7378 | 1 | MODBUS_OUTPUT_AM_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_23
7379 | 1 | MODBUS_OUTPUT_AM_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_24
7380 | 1 | MODBUS_OUTPUT_AM_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_25
7381 | 1 | MODBUS_OUTPUT_AM_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_26
7382 | 1 | MODBUS_OUTPUT_AM_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_27
7383 | 1 | MODBUS_OUTPUT_AM_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_28
7384 | 1 | MODBUS_OUTPUT_AM_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_29
7385 | 1 | MODBUS_OUTPUT_AM_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_30
7386 | 1 | MODBUS_OUTPUT_AM_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_31
7387 | 1 | MODBUS_OUTPUT_AM_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_32
7388 | 1 | MODBUS_OUTPUT_AM_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_33
7389 | 1 | MODBUS_OUTPUT_AM_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_34
7390 | 1 | MODBUS_OUTPUT_AM_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_35
7391 | 1 | MODBUS_OUTPUT_AM_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_36
7392 | 1 | MODBUS_OUTPUT_AM_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_37
7393 | 1 | MODBUS_OUTPUT_AM_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_38
7394 | 1 | MODBUS_OUTPUT_AM_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_39
7395 | 1 | MODBUS_OUTPUT_AM_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_40
7396 | 1 | MODBUS_OUTPUT_AM_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_41
7397 | 1 | MODBUS_OUTPUT_AM_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_42
7398 | 1 | MODBUS_OUTPUT_AM_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_43
7399 | 1 | MODBUS_OUTPUT_AM_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_44
7400 | 1 | MODBUS_OUTPUT_AM_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_45
7401 | 1 | MODBUS_OUTPUT_AM_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_46
7402 | 1 | MODBUS_OUTPUT_AM_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_47
7403 | 1 | MODBUS_OUTPUT_AM_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_48
7404 | 1 | MODBUS_OUTPUT_AM_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_49
7405 | 1 | MODBUS_OUTPUT_AM_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_50
7406 | 1 | MODBUS_OUTPUT_AM_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_51
7407 | 1 | MODBUS_OUTPUT_AM_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_52
7408 | 1 | MODBUS_OUTPUT_AM_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_53
7409 | 1 | MODBUS_OUTPUT_AM_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_54
7410 | 1 | MODBUS_OUTPUT_AM_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_55
7411 | 1 | MODBUS_OUTPUT_AM_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_56
7412 | 1 | MODBUS_OUTPUT_AM_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_57
7413 | 1 | MODBUS_OUTPUT_AM_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_58
7414 | 1 | MODBUS_OUTPUT_AM_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_59
7415 | 1 | MODBUS_OUTPUT_AM_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_60
7416 | 1 | MODBUS_OUTPUT_AM_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_61
7417 | 1 | MODBUS_OUTPUT_AM_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_62
7418 | 1 | MODBUS_OUTPUT_AM_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_63
7419 | 1 | MODBUS_OUTPUT_AM_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_Auto_Manual_64
7420 | 1 | MODBUS_OUTPUT_TYPE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output type, digital or analog (0 - digital 1 - analog)
7421 | 1 | MODBUS_OUTPUT_TYPE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_2
7422 | 1 | MODBUS_OUTPUT_TYPE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_3
7423 | 1 | MODBUS_OUTPUT_TYPE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_4
7424 | 1 | MODBUS_OUTPUT_TYPE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_5
7425 | 1 | MODBUS_OUTPUT_TYPE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_6
7426 | 1 | MODBUS_OUTPUT_TYPE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_7
7427 | 1 | MODBUS_OUTPUT_TYPE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_8
7428 | 1 | MODBUS_OUTPUT_TYPE_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_9
7429 | 1 | MODBUS_OUTPUT_TYPE_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_10
7430 | 1 | MODBUS_OUTPUT_TYPE_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_11
7431 | 1 | MODBUS_OUTPUT_TYPE_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_12
7432 | 1 | MODBUS_OUTPUT_TYPE_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_13
7433 | 1 | MODBUS_OUTPUT_TYPE_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_14
7434 | 1 | MODBUS_OUTPUT_TYPE_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_15
7435 | 1 | MODBUS_OUTPUT_TYPE_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_16
7436 | 1 | MODBUS_OUTPUT_TYPE_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_17
7437 | 1 | MODBUS_OUTPUT_TYPE_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_18
7438 | 1 | MODBUS_OUTPUT_TYPE_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_19
7439 | 1 | MODBUS_OUTPUT_TYPE_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_20
7440 | 1 | MODBUS_OUTPUT_TYPE_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_21
7441 | 1 | MODBUS_OUTPUT_TYPE_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_22
7442 | 1 | MODBUS_OUTPUT_TYPE_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_23
7443 | 1 | MODBUS_OUTPUT_TYPE_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_24
7444 | 1 | MODBUS_OUTPUT_TYPE_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_25
7445 | 1 | MODBUS_OUTPUT_TYPE_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_26
7446 | 1 | MODBUS_OUTPUT_TYPE_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_27
7447 | 1 | MODBUS_OUTPUT_TYPE_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_28
7448 | 1 | MODBUS_OUTPUT_TYPE_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_29
7449 | 1 | MODBUS_OUTPUT_TYPE_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_30
7450 | 1 | MODBUS_OUTPUT_TYPE_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_31
7451 | 1 | MODBUS_OUTPUT_TYPE_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_32
7452 | 1 | MODBUS_OUTPUT_TYPE_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_33
7453 | 1 | MODBUS_OUTPUT_TYPE_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_34
7454 | 1 | MODBUS_OUTPUT_TYPE_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_35
7455 | 1 | MODBUS_OUTPUT_TYPE_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_36
7456 | 1 | MODBUS_OUTPUT_TYPE_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_37
7457 | 1 | MODBUS_OUTPUT_TYPE_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_38
7458 | 1 | MODBUS_OUTPUT_TYPE_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_39
7459 | 1 | MODBUS_OUTPUT_TYPE_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_40
7460 | 1 | MODBUS_OUTPUT_TYPE_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_41
7461 | 1 | MODBUS_OUTPUT_TYPE_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_42
7462 | 1 | MODBUS_OUTPUT_TYPE_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_43
7463 | 1 | MODBUS_OUTPUT_TYPE_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_44
7464 | 1 | MODBUS_OUTPUT_TYPE_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_45
7465 | 1 | MODBUS_OUTPUT_TYPE_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_46
7466 | 1 | MODBUS_OUTPUT_TYPE_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_47
7467 | 1 | MODBUS_OUTPUT_TYPE_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_48
7468 | 1 | MODBUS_OUTPUT_TYPE_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_49
7469 | 1 | MODBUS_OUTPUT_TYPE_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_50
7470 | 1 | MODBUS_OUTPUT_TYPE_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_51
7471 | 1 | MODBUS_OUTPUT_TYPE_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_52
7472 | 1 | MODBUS_OUTPUT_TYPE_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_53
7473 | 1 | MODBUS_OUTPUT_TYPE_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_54
7474 | 1 | MODBUS_OUTPUT_TYPE_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_55
7475 | 1 | MODBUS_OUTPUT_TYPE_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_56
7476 | 1 | MODBUS_OUTPUT_TYPE_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_57
7477 | 1 | MODBUS_OUTPUT_TYPE_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_58
7478 | 1 | MODBUS_OUTPUT_TYPE_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_59
7479 | 1 | MODBUS_OUTPUT_TYPE_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_60
7480 | 1 | MODBUS_OUTPUT_TYPE_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_61
7481 | 1 | MODBUS_OUTPUT_TYPE_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_62
7482 | 1 | MODBUS_OUTPUT_TYPE_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_63
7483 | 1 | MODBUS_OUTPUT_TYPE_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OUTPUT_TYPE_64
7484 | 2 | MODBUS_INPUT_VALUE_1 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_1 eg:high register 7484 . Low register 7485 Value = high_register*65536 + low_register If value is 12345 , all this value divide 1000 . calculate to three decimal places , that means 12.345
7486 | 2 | MODBUS_INPUT_VALUE_2 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_2
7488 | 2 | MODBUS_INPUT_VALUE_3 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_3
7490 | 2 | MODBUS_INPUT_VALUE_4 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_4
7492 | 2 | MODBUS_INPUT_VALUE_5 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_5
7494 | 2 | MODBUS_INPUT_VALUE_6 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_6
7496 | 2 | MODBUS_INPUT_VALUE_7 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_7
7498 | 2 | MODBUS_INPUT_VALUE_8 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_8
7500 | 2 | MODBUS_INPUT_VALUE_9 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_9
7502 | 2 | MODBUS_INPUT_VALUE_10 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_10
7504 | 2 | MODBUS_INPUT_VALUE_11 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_11
7506 | 2 | MODBUS_INPUT_VALUE_12 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_12
7508 | 2 | MODBUS_INPUT_VALUE_13 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_13
7510 | 2 | MODBUS_INPUT_VALUE_14 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_14
7512 | 2 | MODBUS_INPUT_VALUE_15 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_15
7514 | 2 | MODBUS_INPUT_VALUE_16 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_16
7516 | 2 | MODBUS_INPUT_VALUE_17 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_17
7518 | 2 | MODBUS_INPUT_VALUE_18 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_18
7520 | 2 | MODBUS_INPUT_VALUE_19 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_19
7522 | 2 | MODBUS_INPUT_VALUE_20 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_20
7524 | 2 | MODBUS_INPUT_VALUE_21 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_21
7526 | 2 | MODBUS_INPUT_VALUE_22 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_22
7528 | 2 | MODBUS_INPUT_VALUE_23 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_23
7530 | 2 | MODBUS_INPUT_VALUE_24 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_24
7532 | 2 | MODBUS_INPUT_VALUE_25 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_25
7534 | 2 | MODBUS_INPUT_VALUE_26 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_26
7536 | 2 | MODBUS_INPUT_VALUE_27 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_27
7538 | 2 | MODBUS_INPUT_VALUE_28 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_28
7540 | 2 | MODBUS_INPUT_VALUE_29 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_29
7542 | 2 | MODBUS_INPUT_VALUE_30 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_30
7544 | 2 | MODBUS_INPUT_VALUE_31 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_31
7546 | 2 | MODBUS_INPUT_VALUE_32 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_32
7548 | 2 | MODBUS_INPUT_VALUE_33 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_33
7550 | 2 | MODBUS_INPUT_VALUE_34 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_34
7552 | 2 | MODBUS_INPUT_VALUE_35 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_35
7554 | 2 | MODBUS_INPUT_VALUE_36 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_36
7556 | 2 | MODBUS_INPUT_VALUE_37 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_37
7558 | 2 | MODBUS_INPUT_VALUE_38 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_38
7560 | 2 | MODBUS_INPUT_VALUE_39 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_39
7562 | 2 | MODBUS_INPUT_VALUE_40 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_40
7564 | 2 | MODBUS_INPUT_VALUE_41 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_41
7566 | 2 | MODBUS_INPUT_VALUE_42 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_42
7568 | 2 | MODBUS_INPUT_VALUE_43 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_43
7570 | 2 | MODBUS_INPUT_VALUE_44 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_44
7572 | 2 | MODBUS_INPUT_VALUE_45 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_45
7574 | 2 | MODBUS_INPUT_VALUE_46 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_46
7576 | 2 | MODBUS_INPUT_VALUE_47 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_47
7578 | 2 | MODBUS_INPUT_VALUE_48 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_48
7580 | 2 | MODBUS_INPUT_VALUE_49 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_49
7582 | 2 | MODBUS_INPUT_VALUE_50 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_50
7584 | 2 | MODBUS_INPUT_VALUE_51 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_51
7586 | 2 | MODBUS_INPUT_VALUE_52 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_52
7588 | 2 | MODBUS_INPUT_VALUE_53 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_53
7590 | 2 | MODBUS_INPUT_VALUE_54 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_54
7592 | 2 | MODBUS_INPUT_VALUE_55 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_55
7594 | 2 | MODBUS_INPUT_VALUE_56 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_56
7596 | 2 | MODBUS_INPUT_VALUE_57 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_57
7598 | 2 | MODBUS_INPUT_VALUE_58 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_58
7600 | 2 | MODBUS_INPUT_VALUE_59 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_59
7602 | 2 | MODBUS_INPUT_VALUE_60 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_60
7604 | 2 | MODBUS_INPUT_VALUE_61 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_61
7606 | 2 | MODBUS_INPUT_VALUE_62 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_62
7608 | 2 | MODBUS_INPUT_VALUE_63 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_63
7610 | 2 | MODBUS_INPUT_VALUE_64 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | INPUT_VALUE_64
7612 | 1 | MODBUS_INPUT_FILTER_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_1
7613 | 1 | MODBUS_INPUT_FILTER_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_2
7614 | 1 | MODBUS_INPUT_FILTER_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_3
7615 | 1 | MODBUS_INPUT_FILTER_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_4
7616 | 1 | MODBUS_INPUT_FILTER_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_5
7617 | 1 | MODBUS_INPUT_FILTER_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_6
7618 | 1 | MODBUS_INPUT_FILTER_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_7
7619 | 1 | MODBUS_INPUT_FILTER_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_8
7620 | 1 | MODBUS_INPUT_FILTER_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_9
7621 | 1 | MODBUS_INPUT_FILTER_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_10
7622 | 1 | MODBUS_INPUT_FILTER_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_11
7623 | 1 | MODBUS_INPUT_FILTER_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_12
7624 | 1 | MODBUS_INPUT_FILTER_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_13
7625 | 1 | MODBUS_INPUT_FILTER_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_14
7626 | 1 | MODBUS_INPUT_FILTER_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_15
7627 | 1 | MODBUS_INPUT_FILTER_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_16
7628 | 1 | MODBUS_INPUT_FILTER_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_17
7629 | 1 | MODBUS_INPUT_FILTER_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_18
7630 | 1 | MODBUS_INPUT_FILTER_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_19
7631 | 1 | MODBUS_INPUT_FILTER_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_20
7632 | 1 | MODBUS_INPUT_FILTER_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_21
7633 | 1 | MODBUS_INPUT_FILTER_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_22
7634 | 1 | MODBUS_INPUT_FILTER_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_23
7635 | 1 | MODBUS_INPUT_FILTER_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_24
7636 | 1 | MODBUS_INPUT_FILTER_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_25
7637 | 1 | MODBUS_INPUT_FILTER_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_26
7638 | 1 | MODBUS_INPUT_FILTER_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_27
7639 | 1 | MODBUS_INPUT_FILTER_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_28
7640 | 1 | MODBUS_INPUT_FILTER_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_29
7641 | 1 | MODBUS_INPUT_FILTER_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_30
7642 | 1 | MODBUS_INPUT_FILTER_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_31
7643 | 1 | MODBUS_INPUT_FILTER_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_32
7644 | 1 | MODBUS_INPUT_FILTER_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_33
7645 | 1 | MODBUS_INPUT_FILTER_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_34
7646 | 1 | MODBUS_INPUT_FILTER_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_35
7647 | 1 | MODBUS_INPUT_FILTER_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_36
7648 | 1 | MODBUS_INPUT_FILTER_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_37
7649 | 1 | MODBUS_INPUT_FILTER_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_38
7650 | 1 | MODBUS_INPUT_FILTER_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_39
7651 | 1 | MODBUS_INPUT_FILTER_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_40
7652 | 1 | MODBUS_INPUT_FILTER_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_41
7653 | 1 | MODBUS_INPUT_FILTER_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_42
7654 | 1 | MODBUS_INPUT_FILTER_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_43
7655 | 1 | MODBUS_INPUT_FILTER_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_44
7656 | 1 | MODBUS_INPUT_FILTER_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_45
7657 | 1 | MODBUS_INPUT_FILTER_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_46
7658 | 1 | MODBUS_INPUT_FILTER_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_47
7659 | 1 | MODBUS_INPUT_FILTER_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_48
7660 | 1 | MODBUS_INPUT_FILTER_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_49
7661 | 1 | MODBUS_INPUT_FILTER_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_50
7662 | 1 | MODBUS_INPUT_FILTER_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_51
7663 | 1 | MODBUS_INPUT_FILTER_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_52
7664 | 1 | MODBUS_INPUT_FILTER_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_53
7665 | 1 | MODBUS_INPUT_FILTER_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_54
7666 | 1 | MODBUS_INPUT_FILTER_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_55
7667 | 1 | MODBUS_INPUT_FILTER_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_56
7668 | 1 | MODBUS_INPUT_FILTER_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_57
7669 | 1 | MODBUS_INPUT_FILTER_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_58
7670 | 1 | MODBUS_INPUT_FILTER_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_59
7671 | 1 | MODBUS_INPUT_FILTER_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_60
7672 | 1 | MODBUS_INPUT_FILTER_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_61
7673 | 1 | MODBUS_INPUT_FILTER_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_62
7674 | 1 | MODBUS_INPUT_FILTER_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_63
7675 | 1 | MODBUS_INPUT_FILTER_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_FILTER_64
7676 | 1 | MODBUS_INPUT_CALIBRATION_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_1
7677 | 1 | MODBUS_INPUT_CALIBRATION_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_2
7678 | 1 | MODBUS_INPUT_CALIBRATION_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_3
7679 | 1 | MODBUS_INPUT_CALIBRATION_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_4
7680 | 1 | MODBUS_INPUT_CALIBRATION_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_5
7681 | 1 | MODBUS_INPUT_CALIBRATION_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_6
7682 | 1 | MODBUS_INPUT_CALIBRATION_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_7
7683 | 1 | MODBUS_INPUT_CALIBRATION_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_8
7684 | 1 | MODBUS_INPUT_CALIBRATION_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_9
7685 | 1 | MODBUS_INPUT_CALIBRATION_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_10
7686 | 1 | MODBUS_INPUT_CALIBRATION_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_11
7687 | 1 | MODBUS_INPUT_CALIBRATION_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_12
7688 | 1 | MODBUS_INPUT_CALIBRATION_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_13
7689 | 1 | MODBUS_INPUT_CALIBRATION_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_14
7690 | 1 | MODBUS_INPUT_CALIBRATION_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_15
7691 | 1 | MODBUS_INPUT_CALIBRATION_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_16
7692 | 1 | MODBUS_INPUT_CALIBRATION_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_17
7693 | 1 | MODBUS_INPUT_CALIBRATION_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_18
7694 | 1 | MODBUS_INPUT_CALIBRATION_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_19
7695 | 1 | MODBUS_INPUT_CALIBRATION_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_20
7696 | 1 | MODBUS_INPUT_CALIBRATION_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_21
7697 | 1 | MODBUS_INPUT_CALIBRATION_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_22
7698 | 1 | MODBUS_INPUT_CALIBRATION_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_23
7699 | 1 | MODBUS_INPUT_CALIBRATION_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_24
7700 | 1 | MODBUS_INPUT_CALIBRATION_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_25
7701 | 1 | MODBUS_INPUT_CALIBRATION_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_26
7702 | 1 | MODBUS_INPUT_CALIBRATION_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_27
7703 | 1 | MODBUS_INPUT_CALIBRATION_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_28
7704 | 1 | MODBUS_INPUT_CALIBRATION_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_29
7705 | 1 | MODBUS_INPUT_CALIBRATION_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_30
7706 | 1 | MODBUS_INPUT_CALIBRATION_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_31
7707 | 1 | MODBUS_INPUT_CALIBRATION_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_32
7708 | 1 | MODBUS_INPUT_CALIBRATION_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_33
7709 | 1 | MODBUS_INPUT_CALIBRATION_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_34
7710 | 1 | MODBUS_INPUT_CALIBRATION_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_35
7711 | 1 | MODBUS_INPUT_CALIBRATION_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_36
7712 | 1 | MODBUS_INPUT_CALIBRATION_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_37
7713 | 1 | MODBUS_INPUT_CALIBRATION_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_38
7714 | 1 | MODBUS_INPUT_CALIBRATION_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_39
7715 | 1 | MODBUS_INPUT_CALIBRATION_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_40
7716 | 1 | MODBUS_INPUT_CALIBRATION_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_41
7717 | 1 | MODBUS_INPUT_CALIBRATION_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_42
7718 | 1 | MODBUS_INPUT_CALIBRATION_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_43
7719 | 1 | MODBUS_INPUT_CALIBRATION_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_44
7720 | 1 | MODBUS_INPUT_CALIBRATION_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_45
7721 | 1 | MODBUS_INPUT_CALIBRATION_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_46
7722 | 1 | MODBUS_INPUT_CALIBRATION_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_47
7723 | 1 | MODBUS_INPUT_CALIBRATION_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_48
7724 | 1 | MODBUS_INPUT_CALIBRATION_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_49
7725 | 1 | MODBUS_INPUT_CALIBRATION_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_50
7726 | 1 | MODBUS_INPUT_CALIBRATION_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_51
7727 | 1 | MODBUS_INPUT_CALIBRATION_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_52
7728 | 1 | MODBUS_INPUT_CALIBRATION_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_53
7729 | 1 | MODBUS_INPUT_CALIBRATION_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_54
7730 | 1 | MODBUS_INPUT_CALIBRATION_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_55
7731 | 1 | MODBUS_INPUT_CALIBRATION_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_56
7732 | 1 | MODBUS_INPUT_CALIBRATION_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_57
7733 | 1 | MODBUS_INPUT_CALIBRATION_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_58
7734 | 1 | MODBUS_INPUT_CALIBRATION_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_59
7735 | 1 | MODBUS_INPUT_CALIBRATION_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_60
7736 | 1 | MODBUS_INPUT_CALIBRATION_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_61
7737 | 1 | MODBUS_INPUT_CALIBRATION_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_62
7738 | 1 | MODBUS_INPUT_CALIBRATION_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_63
7739 | 1 | MODBUS_INPUT_CALIBRATION_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CALIBRATION_64
7740 | 1 | MODBUS_INPUT_CAL_SIGN_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_1
7741 | 1 | MODBUS_INPUT_CAL_SIGN_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_2
7742 | 1 | MODBUS_INPUT_CAL_SIGN_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_3
7743 | 1 | MODBUS_INPUT_CAL_SIGN_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_4
7744 | 1 | MODBUS_INPUT_CAL_SIGN_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_5
7745 | 1 | MODBUS_INPUT_CAL_SIGN_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_6
7746 | 1 | MODBUS_INPUT_CAL_SIGN_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_7
7747 | 1 | MODBUS_INPUT_CAL_SIGN_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_8
7748 | 1 | MODBUS_INPUT_CAL_SIGN_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_9
7749 | 1 | MODBUS_INPUT_CAL_SIGN_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_10
7750 | 1 | MODBUS_INPUT_CAL_SIGN_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_11
7751 | 1 | MODBUS_INPUT_CAL_SIGN_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_12
7752 | 1 | MODBUS_INPUT_CAL_SIGN_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_13
7753 | 1 | MODBUS_INPUT_CAL_SIGN_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_14
7754 | 1 | MODBUS_INPUT_CAL_SIGN_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_15
7755 | 1 | MODBUS_INPUT_CAL_SIGN_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_16
7756 | 1 | MODBUS_INPUT_CAL_SIGN_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_17
7757 | 1 | MODBUS_INPUT_CAL_SIGN_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_18
7758 | 1 | MODBUS_INPUT_CAL_SIGN_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_19
7759 | 1 | MODBUS_INPUT_CAL_SIGN_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_20
7760 | 1 | MODBUS_INPUT_CAL_SIGN_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_21
7761 | 1 | MODBUS_INPUT_CAL_SIGN_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_22
7762 | 1 | MODBUS_INPUT_CAL_SIGN_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_23
7763 | 1 | MODBUS_INPUT_CAL_SIGN_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_24
7764 | 1 | MODBUS_INPUT_CAL_SIGN_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_25
7765 | 1 | MODBUS_INPUT_CAL_SIGN_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_26
7766 | 1 | MODBUS_INPUT_CAL_SIGN_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_27
7767 | 1 | MODBUS_INPUT_CAL_SIGN_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_28
7768 | 1 | MODBUS_INPUT_CAL_SIGN_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_29
7769 | 1 | MODBUS_INPUT_CAL_SIGN_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_30
7770 | 1 | MODBUS_INPUT_CAL_SIGN_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_31
7771 | 1 | MODBUS_INPUT_CAL_SIGN_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_32
7772 | 1 | MODBUS_INPUT_CAL_SIGN_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_33
7773 | 1 | MODBUS_INPUT_CAL_SIGN_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_34
7774 | 1 | MODBUS_INPUT_CAL_SIGN_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_35
7775 | 1 | MODBUS_INPUT_CAL_SIGN_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_36
7776 | 1 | MODBUS_INPUT_CAL_SIGN_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_37
7777 | 1 | MODBUS_INPUT_CAL_SIGN_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_38
7778 | 1 | MODBUS_INPUT_CAL_SIGN_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_39
7779 | 1 | MODBUS_INPUT_CAL_SIGN_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_40
7780 | 1 | MODBUS_INPUT_CAL_SIGN_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_41
7781 | 1 | MODBUS_INPUT_CAL_SIGN_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_42
7782 | 1 | MODBUS_INPUT_CAL_SIGN_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_43
7783 | 1 | MODBUS_INPUT_CAL_SIGN_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_44
7784 | 1 | MODBUS_INPUT_CAL_SIGN_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_45
7785 | 1 | MODBUS_INPUT_CAL_SIGN_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_46
7786 | 1 | MODBUS_INPUT_CAL_SIGN_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_47
7787 | 1 | MODBUS_INPUT_CAL_SIGN_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_48
7788 | 1 | MODBUS_INPUT_CAL_SIGN_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_49
7789 | 1 | MODBUS_INPUT_CAL_SIGN_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_50
7790 | 1 | MODBUS_INPUT_CAL_SIGN_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_51
7791 | 1 | MODBUS_INPUT_CAL_SIGN_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_52
7792 | 1 | MODBUS_INPUT_CAL_SIGN_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_53
7793 | 1 | MODBUS_INPUT_CAL_SIGN_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_54
7794 | 1 | MODBUS_INPUT_CAL_SIGN_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_55
7795 | 1 | MODBUS_INPUT_CAL_SIGN_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_56
7796 | 1 | MODBUS_INPUT_CAL_SIGN_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_57
7797 | 1 | MODBUS_INPUT_CAL_SIGN_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_58
7798 | 1 | MODBUS_INPUT_CAL_SIGN_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_59
7799 | 1 | MODBUS_INPUT_CAL_SIGN_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_60
7800 | 1 | MODBUS_INPUT_CAL_SIGN_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_61
7801 | 1 | MODBUS_INPUT_CAL_SIGN_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_62
7802 | 1 | MODBUS_INPUT_CAL_SIGN_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_63
7803 | 1 | MODBUS_INPUT_CAL_SIGN_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_CAL_SIGN_64
7804 | 1 | MODBUS_INPUT_RANGE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | high bye is analog or digital (digital is 0, analog is 1), low byte is range. if analog inputs (not_used_input = 0, Y3K_40_150DegC, Y3K_40_300DegF, R10K_40_120DegC, R10K_40_250DegF, R3K_40_150DegC, R3K_40_300DegF, KM10K_40_120DegC, KM10K_40_250DegF, A10K_50_110DegC, A10K_60_200DegF, V0_5, I0_100Amps, I0_20ma, I0_20psi, N0_2_32counts, N0_3000FPM_0_5V, P0_100_0_5V, P0_100_4_20ma, P0_255p_min, table1, table2, table3, table4, table5,100 - HI_SPEED_COUNTER ),
7805 | 1 | MODBUS_INPUT_RANGE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | if digital inputs not_used_input = 0 OFF_ON = 1, CLOSED_OPEN = 2, STOP_START = 3, DISABLED_ENABLED = 4, NORMAL_ALARM = 5, NORMAL_HIGH = 6, NORMAL_LOW = 7, NO_YES = 8, COOL_HEAT = 9, UNOCCUPIED_OCCUPIED = 10, LOW_HIGH = 11, ON_OFF = 12 , OPEN_CLOSED, START_STOP, ENABLED_DISABLED, ALARM_NORMAL, HIGH_NORMAL, LOW_NORMAL, YES_NO, HEAT_COOL, OCCUPIED_UNOCCUPIED, HIGH_LOW, custom_digital1, custom_digital2, custom_digital3, custom_digital4, custom_digital5, custom_digital6, custom_digital7, custom_digital8 )
7806 | 1 | MODBUS_INPUT_RANGE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_3
7807 | 1 | MODBUS_INPUT_RANGE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_4
7808 | 1 | MODBUS_INPUT_RANGE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_5
7809 | 1 | MODBUS_INPUT_RANGE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_6
7810 | 1 | MODBUS_INPUT_RANGE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_7
7811 | 1 | MODBUS_INPUT_RANGE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_8
7812 | 1 | MODBUS_INPUT_RANGE_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_9
7813 | 1 | MODBUS_INPUT_RANGE_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_10
7814 | 1 | MODBUS_INPUT_RANGE_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_11
7815 | 1 | MODBUS_INPUT_RANGE_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_12
7816 | 1 | MODBUS_INPUT_RANGE_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_13
7817 | 1 | MODBUS_INPUT_RANGE_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_14
7818 | 1 | MODBUS_INPUT_RANGE_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_15
7819 | 1 | MODBUS_INPUT_RANGE_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_16
7820 | 1 | MODBUS_INPUT_RANGE_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_17
7821 | 1 | MODBUS_INPUT_RANGE_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_18
7822 | 1 | MODBUS_INPUT_RANGE_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_19
7823 | 1 | MODBUS_INPUT_RANGE_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_20
7824 | 1 | MODBUS_INPUT_RANGE_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_21
7825 | 1 | MODBUS_INPUT_RANGE_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_22
7826 | 1 | MODBUS_INPUT_RANGE_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_23
7827 | 1 | MODBUS_INPUT_RANGE_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_24
7828 | 1 | MODBUS_INPUT_RANGE_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_25
7829 | 1 | MODBUS_INPUT_RANGE_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_26
7830 | 1 | MODBUS_INPUT_RANGE_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_27
7831 | 1 | MODBUS_INPUT_RANGE_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_28
7832 | 1 | MODBUS_INPUT_RANGE_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_29
7833 | 1 | MODBUS_INPUT_RANGE_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_30
7834 | 1 | MODBUS_INPUT_RANGE_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_31
7835 | 1 | MODBUS_INPUT_RANGE_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_32
7836 | 1 | MODBUS_INPUT_RANGE_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_33
7837 | 1 | MODBUS_INPUT_RANGE_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_34
7838 | 1 | MODBUS_INPUT_RANGE_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_35
7839 | 1 | MODBUS_INPUT_RANGE_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_36
7840 | 1 | MODBUS_INPUT_RANGE_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_37
7841 | 1 | MODBUS_INPUT_RANGE_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_38
7842 | 1 | MODBUS_INPUT_RANGE_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_39
7843 | 1 | MODBUS_INPUT_RANGE_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_40
7844 | 1 | MODBUS_INPUT_RANGE_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_41
7845 | 1 | MODBUS_INPUT_RANGE_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_42
7846 | 1 | MODBUS_INPUT_RANGE_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_43
7847 | 1 | MODBUS_INPUT_RANGE_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_44
7848 | 1 | MODBUS_INPUT_RANGE_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_45
7849 | 1 | MODBUS_INPUT_RANGE_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_46
7850 | 1 | MODBUS_INPUT_RANGE_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_47
7851 | 1 | MODBUS_INPUT_RANGE_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_48
7852 | 1 | MODBUS_INPUT_RANGE_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_49
7853 | 1 | MODBUS_INPUT_RANGE_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_50
7854 | 1 | MODBUS_INPUT_RANGE_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_51
7855 | 1 | MODBUS_INPUT_RANGE_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_52
7856 | 1 | MODBUS_INPUT_RANGE_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_53
7857 | 1 | MODBUS_INPUT_RANGE_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_54
7858 | 1 | MODBUS_INPUT_RANGE_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_55
7859 | 1 | MODBUS_INPUT_RANGE_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_56
7860 | 1 | MODBUS_INPUT_RANGE_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_57
7861 | 1 | MODBUS_INPUT_RANGE_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_58
7862 | 1 | MODBUS_INPUT_RANGE_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_59
7863 | 1 | MODBUS_INPUT_RANGE_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_60
7864 | 1 | MODBUS_INPUT_RANGE_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_61
7865 | 1 | MODBUS_INPUT_RANGE_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_62
7866 | 1 | MODBUS_INPUT_RANGE_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_63
7867 | 1 | MODBUS_INPUT_RANGE_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_RANGE_64
7868 | 1 | MODBUS_INPUT_AM_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Auto or Maunual of inputs
7869 | 1 | MODBUS_INPUT_AM_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_2
7870 | 1 | MODBUS_INPUT_AM_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_3
7871 | 1 | MODBUS_INPUT_AM_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_4
7872 | 1 | MODBUS_INPUT_AM_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_5
7873 | 1 | MODBUS_INPUT_AM_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_6
7874 | 1 | MODBUS_INPUT_AM_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_7
7875 | 1 | MODBUS_INPUT_AM_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_8
7876 | 1 | MODBUS_INPUT_AM_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_9
7877 | 1 | MODBUS_INPUT_AM_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_10
7878 | 1 | MODBUS_INPUT_AM_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_11
7879 | 1 | MODBUS_INPUT_AM_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_12
7880 | 1 | MODBUS_INPUT_AM_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_13
7881 | 1 | MODBUS_INPUT_AM_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_14
7882 | 1 | MODBUS_INPUT_AM_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_15
7883 | 1 | MODBUS_INPUT_AM_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_16
7884 | 1 | MODBUS_INPUT_AM_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_17
7885 | 1 | MODBUS_INPUT_AM_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_18
7886 | 1 | MODBUS_INPUT_AM_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_19
7887 | 1 | MODBUS_INPUT_AM_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_20
7888 | 1 | MODBUS_INPUT_AM_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_21
7889 | 1 | MODBUS_INPUT_AM_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_22
7890 | 1 | MODBUS_INPUT_AM_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_23
7891 | 1 | MODBUS_INPUT_AM_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_24
7892 | 1 | MODBUS_INPUT_AM_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_25
7893 | 1 | MODBUS_INPUT_AM_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_26
7894 | 1 | MODBUS_INPUT_AM_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_27
7895 | 1 | MODBUS_INPUT_AM_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_28
7896 | 1 | MODBUS_INPUT_AM_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_29
7897 | 1 | MODBUS_INPUT_AM_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_30
7898 | 1 | MODBUS_INPUT_AM_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_31
7899 | 1 | MODBUS_INPUT_AM_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_32
7900 | 1 | MODBUS_INPUT_AM_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_33
7901 | 1 | MODBUS_INPUT_AM_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_34
7902 | 1 | MODBUS_INPUT_AM_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_35
7903 | 1 | MODBUS_INPUT_AM_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_36
7904 | 1 | MODBUS_INPUT_AM_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_37
7905 | 1 | MODBUS_INPUT_AM_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_38
7906 | 1 | MODBUS_INPUT_AM_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_39
7907 | 1 | MODBUS_INPUT_AM_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_40
7908 | 1 | MODBUS_INPUT_AM_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_41
7909 | 1 | MODBUS_INPUT_AM_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_42
7910 | 1 | MODBUS_INPUT_AM_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_43
7911 | 1 | MODBUS_INPUT_AM_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_44
7912 | 1 | MODBUS_INPUT_AM_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_45
7913 | 1 | MODBUS_INPUT_AM_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_46
7914 | 1 | MODBUS_INPUT_AM_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_47
7915 | 1 | MODBUS_INPUT_AM_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_48
7916 | 1 | MODBUS_INPUT_AM_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_49
7917 | 1 | MODBUS_INPUT_AM_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_50
7918 | 1 | MODBUS_INPUT_AM_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_51
7919 | 1 | MODBUS_INPUT_AM_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_52
7920 | 1 | MODBUS_INPUT_AM_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_53
7921 | 1 | MODBUS_INPUT_AM_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_54
7922 | 1 | MODBUS_INPUT_AM_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_55
7923 | 1 | MODBUS_INPUT_AM_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_56
7924 | 1 | MODBUS_INPUT_AM_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_57
7925 | 1 | MODBUS_INPUT_AM_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_58
7926 | 1 | MODBUS_INPUT_AM_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_59
7927 | 1 | MODBUS_INPUT_AM_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_60
7928 | 1 | MODBUS_INPUT_AM_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_61
7929 | 1 | MODBUS_INPUT_AM_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_62
7930 | 1 | MODBUS_INPUT_AM_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_63
7931 | 1 | MODBUS_INPUT_AM_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_AM_64
7932 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_1 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_1
7934 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_2 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_2
7936 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_3 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_3
7938 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_4 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_4
7940 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_5 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_5
7942 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_6 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_6
7944 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_7 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_7
7946 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_8 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_8
7948 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_9 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_9
7950 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_10 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_10
7952 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_11 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_11
7954 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_12 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_12
7956 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_13 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_13
7958 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_14 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_14
7960 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_15 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_15
7962 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_16 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_16
7964 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_17 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_17
7966 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_18 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_18
7968 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_19 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_19
7970 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_20 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_20
7972 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_21 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_21
7974 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_22 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_22
7976 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_23 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_23
7978 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_24 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_24
7980 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_25 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_25
7982 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_26 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_26
7984 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_27 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_27
7986 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_28 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_28
7988 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_29 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_29
7990 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_30 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_30
7992 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_31 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_31
7994 | 2 | MODBUS_INPUT_HI_SPD_COUNTER_32 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | HI_SPD_COUNTER_32
7996 | 1 | MODBUS_INPUT_HI_SPD_EN_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ENABLE high speed counter,( START - 0, STOP - 1)
7997 | 1 | MODBUS_INPUT_HI_SPD_EN_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_2
7998 | 1 | MODBUS_INPUT_HI_SPD_EN_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_3
7999 | 1 | MODBUS_INPUT_HI_SPD_EN_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_4
8000 | 1 | MODBUS_INPUT_HI_SPD_EN_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_5
8001 | 1 | MODBUS_INPUT_HI_SPD_EN_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_6
8002 | 1 | MODBUS_INPUT_HI_SPD_EN_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_7
8003 | 1 | MODBUS_INPUT_HI_SPD_EN_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_8
8004 | 1 | MODBUS_INPUT_HI_SPD_EN_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_9
8005 | 1 | MODBUS_INPUT_HI_SPD_EN_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_10
8006 | 1 | MODBUS_INPUT_HI_SPD_EN_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_11
8007 | 1 | MODBUS_INPUT_HI_SPD_EN_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_12
8008 | 1 | MODBUS_INPUT_HI_SPD_EN_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_13
8009 | 1 | MODBUS_INPUT_HI_SPD_EN_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_14
8010 | 1 | MODBUS_INPUT_HI_SPD_EN_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_15
8011 | 1 | MODBUS_INPUT_HI_SPD_EN_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_16
8012 | 1 | MODBUS_INPUT_HI_SPD_EN_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_17
8013 | 1 | MODBUS_INPUT_HI_SPD_EN_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_18
8014 | 1 | MODBUS_INPUT_HI_SPD_EN_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_19
8015 | 1 | MODBUS_INPUT_HI_SPD_EN_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_20
8016 | 1 | MODBUS_INPUT_HI_SPD_EN_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_21
8017 | 1 | MODBUS_INPUT_HI_SPD_EN_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_22
8018 | 1 | MODBUS_INPUT_HI_SPD_EN_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_23
8019 | 1 | MODBUS_INPUT_HI_SPD_EN_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_24
8020 | 1 | MODBUS_INPUT_HI_SPD_EN_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_25
8021 | 1 | MODBUS_INPUT_HI_SPD_EN_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_26
8022 | 1 | MODBUS_INPUT_HI_SPD_EN_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_27
8023 | 1 | MODBUS_INPUT_HI_SPD_EN_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_28
8024 | 1 | MODBUS_INPUT_HI_SPD_EN_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_29
8025 | 1 | MODBUS_INPUT_HI_SPD_EN_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_30
8026 | 1 | MODBUS_INPUT_HI_SPD_EN_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_31
8027 | 1 | MODBUS_INPUT_HI_SPD_EN_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_HI_SPD_EN_32
8028 | 1 | MODBUS_INPUT_TYPE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Input type, 0- thermistor, 1- 5v, 2-10v, 3- 20ma
8029 | 1 | MODBUS_INPUT_TYPE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_2
8030 | 1 | MODBUS_INPUT_TYPE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_3
8031 | 1 | MODBUS_INPUT_TYPE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_4
8032 | 1 | MODBUS_INPUT_TYPE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_5
8033 | 1 | MODBUS_INPUT_TYPE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_6
8034 | 1 | MODBUS_INPUT_TYPE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_7
8035 | 1 | MODBUS_INPUT_TYPE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_8
8036 | 1 | MODBUS_INPUT_TYPE_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_9
8037 | 1 | MODBUS_INPUT_TYPE_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_10
8038 | 1 | MODBUS_INPUT_TYPE_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_11
8039 | 1 | MODBUS_INPUT_TYPE_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_12
8040 | 1 | MODBUS_INPUT_TYPE_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_13
8041 | 1 | MODBUS_INPUT_TYPE_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_14
8042 | 1 | MODBUS_INPUT_TYPE_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_15
8043 | 1 | MODBUS_INPUT_TYPE_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_16
8044 | 1 | MODBUS_INPUT_TYPE_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_17
8045 | 1 | MODBUS_INPUT_TYPE_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_18
8046 | 1 | MODBUS_INPUT_TYPE_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_19
8047 | 1 | MODBUS_INPUT_TYPE_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_20
8048 | 1 | MODBUS_INPUT_TYPE_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_21
8049 | 1 | MODBUS_INPUT_TYPE_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_22
8050 | 1 | MODBUS_INPUT_TYPE_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_23
8051 | 1 | MODBUS_INPUT_TYPE_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_24
8052 | 1 | MODBUS_INPUT_TYPE_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_25
8053 | 1 | MODBUS_INPUT_TYPE_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_26
8054 | 1 | MODBUS_INPUT_TYPE_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_27
8055 | 1 | MODBUS_INPUT_TYPE_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_28
8056 | 1 | MODBUS_INPUT_TYPE_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_29
8057 | 1 | MODBUS_INPUT_TYPE_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_30
8058 | 1 | MODBUS_INPUT_TYPE_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_31
8059 | 1 | MODBUS_INPUT_TYPE_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_32
8060 | 1 | MODBUS_INPUT_TYPE_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_33
8061 | 1 | MODBUS_INPUT_TYPE_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_34
8062 | 1 | MODBUS_INPUT_TYPE_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_35
8063 | 1 | MODBUS_INPUT_TYPE_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_36
8064 | 1 | MODBUS_INPUT_TYPE_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_37
8065 | 1 | MODBUS_INPUT_TYPE_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_38
8066 | 1 | MODBUS_INPUT_TYPE_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_39
8067 | 1 | MODBUS_INPUT_TYPE_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_40
8068 | 1 | MODBUS_INPUT_TYPE_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_41
8069 | 1 | MODBUS_INPUT_TYPE_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_42
8070 | 1 | MODBUS_INPUT_TYPE_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_43
8071 | 1 | MODBUS_INPUT_TYPE_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_44
8072 | 1 | MODBUS_INPUT_TYPE_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_45
8073 | 1 | MODBUS_INPUT_TYPE_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_46
8074 | 1 | MODBUS_INPUT_TYPE_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_47
8075 | 1 | MODBUS_INPUT_TYPE_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_48
8076 | 1 | MODBUS_INPUT_TYPE_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_49
8077 | 1 | MODBUS_INPUT_TYPE_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_50
8078 | 1 | MODBUS_INPUT_TYPE_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_51
8079 | 1 | MODBUS_INPUT_TYPE_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_52
8080 | 1 | MODBUS_INPUT_TYPE_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_53
8081 | 1 | MODBUS_INPUT_TYPE_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_54
8082 | 1 | MODBUS_INPUT_TYPE_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_55
8083 | 1 | MODBUS_INPUT_TYPE_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_56
8084 | 1 | MODBUS_INPUT_TYPE_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_57
8085 | 1 | MODBUS_INPUT_TYPE_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_58
8086 | 1 | MODBUS_INPUT_TYPE_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_59
8087 | 1 | MODBUS_INPUT_TYPE_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_60
8088 | 1 | MODBUS_INPUT_TYPE_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_61
8089 | 1 | MODBUS_INPUT_TYPE_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_62
8090 | 1 | MODBUS_INPUT_TYPE_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_63
8091 | 1 | MODBUS_INPUT_TYPE_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | INPUT_TYPE_64
8092 | 2 | MODBUS_VAR_VALUE_1 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_1 eg:high register 8092 . Low register 8093 Value = high_register*65536 + low_register If value is 12345 , all this value divide 1000 . calculate to three decimal places , that means 12.345
8094 | 2 | MODBUS_VAR_VALUE_2 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_2
8096 | 2 | MODBUS_VAR_VALUE_3 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_3
8098 | 2 | MODBUS_VAR_VALUE_4 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_4
8100 | 2 | MODBUS_VAR_VALUE_5 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_5
8102 | 2 | MODBUS_VAR_VALUE_6 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_6
8104 | 2 | MODBUS_VAR_VALUE_7 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_7
8106 | 2 | MODBUS_VAR_VALUE_8 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_8
8108 | 2 | MODBUS_VAR_VALUE_9 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_9
8110 | 2 | MODBUS_VAR_VALUE_10 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_10
8112 | 2 | MODBUS_VAR_VALUE_11 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_11
8114 | 2 | MODBUS_VAR_VALUE_12 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_12
8116 | 2 | MODBUS_VAR_VALUE_13 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_13
8118 | 2 | MODBUS_VAR_VALUE_14 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_14
8120 | 2 | MODBUS_VAR_VALUE_15 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_15
8122 | 2 | MODBUS_VAR_VALUE_16 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_16
8124 | 2 | MODBUS_VAR_VALUE_17 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_17
8126 | 2 | MODBUS_VAR_VALUE_18 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_18
8128 | 2 | MODBUS_VAR_VALUE_19 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_19
8130 | 2 | MODBUS_VAR_VALUE_20 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_20
8132 | 2 | MODBUS_VAR_VALUE_21 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_21
8134 | 2 | MODBUS_VAR_VALUE_22 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_22
8136 | 2 | MODBUS_VAR_VALUE_23 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_23
8138 | 2 | MODBUS_VAR_VALUE_24 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_24
8140 | 2 | MODBUS_VAR_VALUE_25 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_25
8142 | 2 | MODBUS_VAR_VALUE_26 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_26
8144 | 2 | MODBUS_VAR_VALUE_27 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_27
8146 | 2 | MODBUS_VAR_VALUE_28 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_28
8148 | 2 | MODBUS_VAR_VALUE_29 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_29
8150 | 2 | MODBUS_VAR_VALUE_30 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_30
8152 | 2 | MODBUS_VAR_VALUE_31 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_31
8154 | 2 | MODBUS_VAR_VALUE_32 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_32
8156 | 2 | MODBUS_VAR_VALUE_33 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_33
8158 | 2 | MODBUS_VAR_VALUE_34 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_34
8160 | 2 | MODBUS_VAR_VALUE_35 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_35
8162 | 2 | MODBUS_VAR_VALUE_36 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_36
8164 | 2 | MODBUS_VAR_VALUE_37 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_37
8166 | 2 | MODBUS_VAR_VALUE_38 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_38
8168 | 2 | MODBUS_VAR_VALUE_39 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_39
8170 | 2 | MODBUS_VAR_VALUE_40 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_40
8172 | 2 | MODBUS_VAR_VALUE_41 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_41
8174 | 2 | MODBUS_VAR_VALUE_42 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_42
8176 | 2 | MODBUS_VAR_VALUE_43 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_43
8178 | 2 | MODBUS_VAR_VALUE_44 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_44
8180 | 2 | MODBUS_VAR_VALUE_45 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_45
8182 | 2 | MODBUS_VAR_VALUE_46 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_46
8184 | 2 | MODBUS_VAR_VALUE_47 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_47
8186 | 2 | MODBUS_VAR_VALUE_48 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_48
8188 | 2 | MODBUS_VAR_VALUE_49 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_49
8190 | 2 | MODBUS_VAR_VALUE_50 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_50
8192 | 2 | MODBUS_VAR_VALUE_51 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_51
8194 | 2 | MODBUS_VAR_VALUE_52 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_52
8196 | 2 | MODBUS_VAR_VALUE_53 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_53
8198 | 2 | MODBUS_VAR_VALUE_54 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_54
8200 | 2 | MODBUS_VAR_VALUE_55 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_55
8202 | 2 | MODBUS_VAR_VALUE_56 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_56
8204 | 2 | MODBUS_VAR_VALUE_57 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_57
8206 | 2 | MODBUS_VAR_VALUE_58 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_58
8208 | 2 | MODBUS_VAR_VALUE_59 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_59
8210 | 2 | MODBUS_VAR_VALUE_60 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_60
8212 | 2 | MODBUS_VAR_VALUE_61 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_61
8214 | 2 | MODBUS_VAR_VALUE_62 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_62
8216 | 2 | MODBUS_VAR_VALUE_63 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_63
8218 | 2 | MODBUS_VAR_VALUE_64 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_64
8220 | 2 | MODBUS_VAR_VALUE_65 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_65
8222 | 2 | MODBUS_VAR_VALUE_66 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_66
8224 | 2 | MODBUS_VAR_VALUE_67 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_67
8226 | 2 | MODBUS_VAR_VALUE_68 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_68
8228 | 2 | MODBUS_VAR_VALUE_69 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_69
8230 | 2 | MODBUS_VAR_VALUE_70 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_70
8232 | 2 | MODBUS_VAR_VALUE_71 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_71
8234 | 2 | MODBUS_VAR_VALUE_72 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_72
8236 | 2 | MODBUS_VAR_VALUE_73 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_73
8238 | 2 | MODBUS_VAR_VALUE_74 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_74
8240 | 2 | MODBUS_VAR_VALUE_75 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_75
8242 | 2 | MODBUS_VAR_VALUE_76 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_76
8244 | 2 | MODBUS_VAR_VALUE_77 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_77
8246 | 2 | MODBUS_VAR_VALUE_78 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_78
8248 | 2 | MODBUS_VAR_VALUE_79 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_79
8250 | 2 | MODBUS_VAR_VALUE_80 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_80
8252 | 2 | MODBUS_VAR_VALUE_81 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_81
8254 | 2 | MODBUS_VAR_VALUE_82 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_82
8256 | 2 | MODBUS_VAR_VALUE_83 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_83
8258 | 2 | MODBUS_VAR_VALUE_84 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_84
8260 | 2 | MODBUS_VAR_VALUE_85 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_85
8262 | 2 | MODBUS_VAR_VALUE_86 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_86
8264 | 2 | MODBUS_VAR_VALUE_87 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_87
8266 | 2 | MODBUS_VAR_VALUE_88 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_88
8268 | 2 | MODBUS_VAR_VALUE_89 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_89
8270 | 2 | MODBUS_VAR_VALUE_90 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_90
8272 | 2 | MODBUS_VAR_VALUE_91 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_91
8274 | 2 | MODBUS_VAR_VALUE_92 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_92
8276 | 2 | MODBUS_VAR_VALUE_93 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_93
8278 | 2 | MODBUS_VAR_VALUE_94 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_94
8280 | 2 | MODBUS_VAR_VALUE_95 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_95
8282 | 2 | MODBUS_VAR_VALUE_96 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_96
8284 | 2 | MODBUS_VAR_VALUE_97 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_97
8286 | 2 | MODBUS_VAR_VALUE_98 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_98
8288 | 2 | MODBUS_VAR_VALUE_99 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_99
8290 | 2 | MODBUS_VAR_VALUE_100 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_100
8292 | 2 | MODBUS_VAR_VALUE_101 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_101
8294 | 2 | MODBUS_VAR_VALUE_102 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_102
8296 | 2 | MODBUS_VAR_VALUE_103 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_103
8298 | 2 | MODBUS_VAR_VALUE_104 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_104
8300 | 2 | MODBUS_VAR_VALUE_105 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_105
8302 | 2 | MODBUS_VAR_VALUE_106 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_106
8304 | 2 | MODBUS_VAR_VALUE_107 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_107
8306 | 2 | MODBUS_VAR_VALUE_108 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_108
8308 | 2 | MODBUS_VAR_VALUE_109 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_109
8310 | 2 | MODBUS_VAR_VALUE_110 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_110
8312 | 2 | MODBUS_VAR_VALUE_111 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_111
8314 | 2 | MODBUS_VAR_VALUE_112 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_112
8316 | 2 | MODBUS_VAR_VALUE_113 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_113
8318 | 2 | MODBUS_VAR_VALUE_114 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_114
8320 | 2 | MODBUS_VAR_VALUE_115 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_115
8322 | 2 | MODBUS_VAR_VALUE_116 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_116
8324 | 2 | MODBUS_VAR_VALUE_117 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_117
8326 | 2 | MODBUS_VAR_VALUE_118 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_118
8328 | 2 | MODBUS_VAR_VALUE_119 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_119
8330 | 2 | MODBUS_VAR_VALUE_120 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_120
8332 | 2 | MODBUS_VAR_VALUE_121 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_121
8334 | 2 | MODBUS_VAR_VALUE_122 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_122
8336 | 2 | MODBUS_VAR_VALUE_123 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_123
8338 | 2 | MODBUS_VAR_VALUE_124 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_124
8340 | 2 | MODBUS_VAR_VALUE_125 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_125
8342 | 2 | MODBUS_VAR_VALUE_126 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_126
8344 | 2 | MODBUS_VAR_VALUE_127 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_127
8346 | 2 | MODBUS_VAR_VALUE_128 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | VAR_VALUE_128
8348 | 1 | MODBUS_VAR_AM_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Auto or Maunual of variables
8349 | 1 | MODBUS_VAR_AM_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_2
8350 | 1 | MODBUS_VAR_AM_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_3
8351 | 1 | MODBUS_VAR_AM_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_4
8352 | 1 | MODBUS_VAR_AM_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_5
8353 | 1 | MODBUS_VAR_AM_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_6
8354 | 1 | MODBUS_VAR_AM_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_7
8355 | 1 | MODBUS_VAR_AM_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_8
8356 | 1 | MODBUS_VAR_AM_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_9
8357 | 1 | MODBUS_VAR_AM_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_10
8358 | 1 | MODBUS_VAR_AM_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_11
8359 | 1 | MODBUS_VAR_AM_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_12
8360 | 1 | MODBUS_VAR_AM_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_13
8361 | 1 | MODBUS_VAR_AM_14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_14
8362 | 1 | MODBUS_VAR_AM_15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_15
8363 | 1 | MODBUS_VAR_AM_16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_16
8364 | 1 | MODBUS_VAR_AM_17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_17
8365 | 1 | MODBUS_VAR_AM_18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_18
8366 | 1 | MODBUS_VAR_AM_19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_19
8367 | 1 | MODBUS_VAR_AM_20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_20
8368 | 1 | MODBUS_VAR_AM_21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_21
8369 | 1 | MODBUS_VAR_AM_22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_22
8370 | 1 | MODBUS_VAR_AM_23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_23
8371 | 1 | MODBUS_VAR_AM_24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_24
8372 | 1 | MODBUS_VAR_AM_25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_25
8373 | 1 | MODBUS_VAR_AM_26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_26
8374 | 1 | MODBUS_VAR_AM_27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_27
8375 | 1 | MODBUS_VAR_AM_28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_28
8376 | 1 | MODBUS_VAR_AM_29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_29
8377 | 1 | MODBUS_VAR_AM_30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_30
8378 | 1 | MODBUS_VAR_AM_31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_31
8379 | 1 | MODBUS_VAR_AM_32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_32
8380 | 1 | MODBUS_VAR_AM_33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_33
8381 | 1 | MODBUS_VAR_AM_34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_34
8382 | 1 | MODBUS_VAR_AM_35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_35
8383 | 1 | MODBUS_VAR_AM_36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_36
8384 | 1 | MODBUS_VAR_AM_37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_37
8385 | 1 | MODBUS_VAR_AM_38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_38
8386 | 1 | MODBUS_VAR_AM_39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_39
8387 | 1 | MODBUS_VAR_AM_40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_40
8388 | 1 | MODBUS_VAR_AM_41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_41
8389 | 1 | MODBUS_VAR_AM_42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_42
8390 | 1 | MODBUS_VAR_AM_43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_43
8391 | 1 | MODBUS_VAR_AM_44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_44
8392 | 1 | MODBUS_VAR_AM_45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_45
8393 | 1 | MODBUS_VAR_AM_46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_46
8394 | 1 | MODBUS_VAR_AM_47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_47
8395 | 1 | MODBUS_VAR_AM_48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_48
8396 | 1 | MODBUS_VAR_AM_49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_49
8397 | 1 | MODBUS_VAR_AM_50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_50
8398 | 1 | MODBUS_VAR_AM_51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_51
8399 | 1 | MODBUS_VAR_AM_52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_52
8400 | 1 | MODBUS_VAR_AM_53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_53
8401 | 1 | MODBUS_VAR_AM_54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_54
8402 | 1 | MODBUS_VAR_AM_55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_55
8403 | 1 | MODBUS_VAR_AM_56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_56
8404 | 1 | MODBUS_VAR_AM_57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_57
8405 | 1 | MODBUS_VAR_AM_58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_58
8406 | 1 | MODBUS_VAR_AM_59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_59
8407 | 1 | MODBUS_VAR_AM_60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_60
8408 | 1 | MODBUS_VAR_AM_61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_61
8409 | 1 | MODBUS_VAR_AM_62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_62
8410 | 1 | MODBUS_VAR_AM_63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_63
8411 | 1 | MODBUS_VAR_AM_64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_64
8412 | 1 | MODBUS_VAR_AM_65 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_65
8413 | 1 | MODBUS_VAR_AM_66 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_66
8414 | 1 | MODBUS_VAR_AM_67 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_67
8415 | 1 | MODBUS_VAR_AM_68 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_68
8416 | 1 | MODBUS_VAR_AM_69 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_69
8417 | 1 | MODBUS_VAR_AM_70 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_70
8418 | 1 | MODBUS_VAR_AM_71 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_71
8419 | 1 | MODBUS_VAR_AM_72 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_72
8420 | 1 | MODBUS_VAR_AM_73 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_73
8421 | 1 | MODBUS_VAR_AM_74 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_74
8422 | 1 | MODBUS_VAR_AM_75 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_75
8423 | 1 | MODBUS_VAR_AM_76 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_76
8424 | 1 | MODBUS_VAR_AM_77 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_77
8425 | 1 | MODBUS_VAR_AM_78 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_78
8426 | 1 | MODBUS_VAR_AM_79 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_79
8427 | 1 | MODBUS_VAR_AM_80 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_80
8428 | 1 | MODBUS_VAR_AM_81 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_81
8429 | 1 | MODBUS_VAR_AM_82 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_82
8430 | 1 | MODBUS_VAR_AM_83 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_83
8431 | 1 | MODBUS_VAR_AM_84 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_84
8432 | 1 | MODBUS_VAR_AM_85 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_85
8433 | 1 | MODBUS_VAR_AM_86 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_86
8434 | 1 | MODBUS_VAR_AM_87 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_87
8435 | 1 | MODBUS_VAR_AM_88 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_88
8436 | 1 | MODBUS_VAR_AM_89 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_89
8437 | 1 | MODBUS_VAR_AM_90 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_90
8438 | 1 | MODBUS_VAR_AM_91 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_91
8439 | 1 | MODBUS_VAR_AM_92 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_92
8440 | 1 | MODBUS_VAR_AM_93 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_93
8441 | 1 | MODBUS_VAR_AM_94 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_94
8442 | 1 | MODBUS_VAR_AM_95 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_95
8443 | 1 | MODBUS_VAR_AM_96 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_96
8444 | 1 | MODBUS_VAR_AM_97 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_97
8445 | 1 | MODBUS_VAR_AM_98 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_98
8446 | 1 | MODBUS_VAR_AM_99 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_99
8447 | 1 | MODBUS_VAR_AM_100 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_100
8448 | 1 | MODBUS_VAR_AM_101 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_101
8449 | 1 | MODBUS_VAR_AM_102 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_102
8450 | 1 | MODBUS_VAR_AM_103 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_103
8451 | 1 | MODBUS_VAR_AM_104 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_104
8452 | 1 | MODBUS_VAR_AM_105 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_105
8453 | 1 | MODBUS_VAR_AM_106 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_106
8454 | 1 | MODBUS_VAR_AM_107 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_107
8455 | 1 | MODBUS_VAR_AM_108 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_108
8456 | 1 | MODBUS_VAR_AM_109 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_109
8457 | 1 | MODBUS_VAR_AM_110 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_110
8458 | 1 | MODBUS_VAR_AM_111 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_111
8459 | 1 | MODBUS_VAR_AM_112 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_112
8460 | 1 | MODBUS_VAR_AM_113 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_113
8461 | 1 | MODBUS_VAR_AM_114 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_114
8462 | 1 | MODBUS_VAR_AM_115 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_115
8463 | 1 | MODBUS_VAR_AM_116 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_116
8464 | 1 | MODBUS_VAR_AM_117 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_117
8465 | 1 | MODBUS_VAR_AM_118 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_118
8466 | 1 | MODBUS_VAR_AM_119 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_119
8467 | 1 | MODBUS_VAR_AM_120 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_120
8468 | 1 | MODBUS_VAR_AM_121 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_121
8469 | 1 | MODBUS_VAR_AM_122 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_122
8470 | 1 | MODBUS_VAR_AM_123 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_123
8471 | 1 | MODBUS_VAR_AM_124 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_124
8472 | 1 | MODBUS_VAR_AM_125 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_125
8473 | 1 | MODBUS_VAR_AM_126 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_126
8474 | 1 | MODBUS_VAR_AM_127 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_127
8475 | 1 | MODBUS_VAR_AM_128 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VAR_AM_128
8476 | 1 | MODBUS_WEEKLYRROUTINE_AM_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | A/M of weekly_roution (0 - auto, 1- manual)
8477 | 1 | MODBUS_WEEKLYRROUTINE_AM_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_2
8478 | 1 | MODBUS_WEEKLYRROUTINE_AM_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_3
8479 | 1 | MODBUS_WEEKLYRROUTINE_AM_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_4
8480 | 1 | MODBUS_WEEKLYRROUTINE_AM_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_5
8481 | 1 | MODBUS_WEEKLYRROUTINE_AM_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_6
8482 | 1 | MODBUS_WEEKLYRROUTINE_AM_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_7
8483 | 1 | MODBUS_WEEKLYRROUTINE_AM_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WEEKLYRROUTINE_AM_8
8484 | 1 | MODBUS_WR_OUT_VALUE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | value of weekly roution
8485 | 1 | MODBUS_WR_OUT_VALUE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_2
8486 | 1 | MODBUS_WR_OUT_VALUE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_3
8487 | 1 | MODBUS_WR_OUT_VALUE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_4
8488 | 1 | MODBUS_WR_OUT_VALUE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_5
8489 | 1 | MODBUS_WR_OUT_VALUE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_6
8490 | 1 | MODBUS_WR_OUT_VALUE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_7
8491 | 1 | MODBUS_WR_OUT_VALUE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_OUT_VALUE_8
8492 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Holiday1 of weekly roution
8493 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_2
8494 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_3
8495 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_4
8496 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_5
8497 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_6
8498 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_7
8499 | 1 | MODBUS_WR_HOLIDAY1_ROUTINE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY1_ROUTINE_8
8500 | 1 | MODBUS_WR_STATE1_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | holiday1 state of weekly roution
8501 | 1 | MODBUS_WR_STATE1_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_2
8502 | 1 | MODBUS_WR_STATE1_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_3
8503 | 1 | MODBUS_WR_STATE1_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_4
8504 | 1 | MODBUS_WR_STATE1_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_5
8505 | 1 | MODBUS_WR_STATE1_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_6
8506 | 1 | MODBUS_WR_STATE1_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_7
8507 | 1 | MODBUS_WR_STATE1_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE1_8
8508 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | holiday2 of weekly roution
8509 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_2
8510 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_3
8511 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_4
8512 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_5
8513 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_6
8514 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_7
8515 | 1 | MODBUS_WR_HOLIDAY2_ROUTINE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_HOLIDAY2_ROUTINE_8
8516 | 1 | MODBUS_WR_STATE2_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | holiday2 state of weekly roution
8517 | 1 | MODBUS_WR_STATE2_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_2
8518 | 1 | MODBUS_WR_STATE2_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_3
8519 | 1 | MODBUS_WR_STATE2_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_4
8520 | 1 | MODBUS_WR_STATE2_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_5
8521 | 1 | MODBUS_WR_STATE2_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_6
8522 | 1 | MODBUS_WR_STATE2_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_7
8523 | 1 | MODBUS_WR_STATE2_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WR_STATE2_8
8524 | 1 | MODBUS_AR_AM_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | A/M of Aunnal_roution (0 - auto, 1- manual)
8525 | 1 | MODBUS_AR_AM_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_AM_2
8526 | 1 | MODBUS_AR_AM_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_AM_3
8527 | 1 | MODBUS_AR_AM_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_AM_4
8528 | 1 | MODBUS_AR_OUT_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | value of Aunnal roution
8529 | 1 | MODBUS_AR_OUT_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_OUT_2
8530 | 1 | MODBUS_AR_OUT_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_OUT_3
8531 | 1 | MODBUS_AR_OUT_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AR_OUT_4
8532 | 1 | MODBUS_VAR_RANGE1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | if it is analog{ unused = 0, degC, degF, FPM, Pa, KPa, psi, in_w, Watts, KW, KWH, Volts, KV, Amps, ma, CFM, Sec, Min, Hours, Days, time_unit, ohms, procent, RH, ppm, counts, Open, CFH, GPM, GPH, GAL, CF, BTU, CMH, custom1, custom2, custom3, custom4, custom5, custom6, custom7, custom8 } if it is digital{ UNUSED = 0, OFF_ON, CLOSED_OPEN, STOP_START, DISABLED_ENABLED, NORMAL_ALARM, NORMAL_HIGH, NORMAL_LOW, NO_YES, COOL_HEAT, UNOCCUPIED_OCCUPIED, LOW_HIGH, ON_OFF , OPEN_CLOSED, START_STOP, ENABLED_DISABLED, ALARM_NORMAL, HIGH_NORMAL, LOW_NORMAL, YES_NO, HEAT_COOL, OCCUPIED_UNOCCUPIED, HIGH_LOW, custom_digital1, custom_digital2, custom_digital3, custom_digital4, custom_digital5, custom_digital6, custom_digital7, custom_digital8 }
8533 | 1 | MODBUS_VAR_RANGE2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8534 | 1 | MODBUS_VAR_RANGE3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8535 | 1 | MODBUS_VAR_RANGE4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8536 | 1 | MODBUS_VAR_RANGE5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8537 | 1 | MODBUS_VAR_RANGE6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8538 | 1 | MODBUS_VAR_RANGE7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8539 | 1 | MODBUS_VAR_RANGE8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8540 | 1 | MODBUS_VAR_RANGE9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8541 | 1 | MODBUS_VAR_RANGE10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8542 | 1 | MODBUS_VAR_RANGE11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8543 | 1 | MODBUS_VAR_RANGE12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8544 | 1 | MODBUS_VAR_RANGE13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8545 | 1 | MODBUS_VAR_RANGE14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8546 | 1 | MODBUS_VAR_RANGE15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8547 | 1 | MODBUS_VAR_RANGE16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8548 | 1 | MODBUS_VAR_RANGE17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8549 | 1 | MODBUS_VAR_RANGE18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8550 | 1 | MODBUS_VAR_RANGE19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8551 | 1 | MODBUS_VAR_RANGE20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8552 | 1 | MODBUS_VAR_RANGE21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8553 | 1 | MODBUS_VAR_RANGE22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8554 | 1 | MODBUS_VAR_RANGE23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8555 | 1 | MODBUS_VAR_RANGE24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8556 | 1 | MODBUS_VAR_RANGE25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8557 | 1 | MODBUS_VAR_RANGE26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8558 | 1 | MODBUS_VAR_RANGE27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8559 | 1 | MODBUS_VAR_RANGE28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8560 | 1 | MODBUS_VAR_RANGE29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8561 | 1 | MODBUS_VAR_RANGE30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8562 | 1 | MODBUS_VAR_RANGE31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8563 | 1 | MODBUS_VAR_RANGE32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8564 | 1 | MODBUS_VAR_RANGE33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8565 | 1 | MODBUS_VAR_RANGE34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8566 | 1 | MODBUS_VAR_RANGE35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8567 | 1 | MODBUS_VAR_RANGE36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8568 | 1 | MODBUS_VAR_RANGE37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8569 | 1 | MODBUS_VAR_RANGE38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8570 | 1 | MODBUS_VAR_RANGE39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8571 | 1 | MODBUS_VAR_RANGE40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8572 | 1 | MODBUS_VAR_RANGE41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8573 | 1 | MODBUS_VAR_RANGE42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8574 | 1 | MODBUS_VAR_RANGE43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8575 | 1 | MODBUS_VAR_RANGE44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8576 | 1 | MODBUS_VAR_RANGE45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8577 | 1 | MODBUS_VAR_RANGE46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8578 | 1 | MODBUS_VAR_RANGE47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8579 | 1 | MODBUS_VAR_RANGE48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8580 | 1 | MODBUS_VAR_RANGE49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8581 | 1 | MODBUS_VAR_RANGE50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8582 | 1 | MODBUS_VAR_RANGE51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8583 | 1 | MODBUS_VAR_RANGE52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8584 | 1 | MODBUS_VAR_RANGE53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8585 | 1 | MODBUS_VAR_RANGE54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8586 | 1 | MODBUS_VAR_RANGE55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8587 | 1 | MODBUS_VAR_RANGE56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8588 | 1 | MODBUS_VAR_RANGE57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8589 | 1 | MODBUS_VAR_RANGE58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8590 | 1 | MODBUS_VAR_RANGE59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8591 | 1 | MODBUS_VAR_RANGE60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8592 | 1 | MODBUS_VAR_RANGE61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8593 | 1 | MODBUS_VAR_RANGE62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8594 | 1 | MODBUS_VAR_RANGE63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8595 | 1 | MODBUS_VAR_RANGE64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8596 | 1 | MODBUS_VAR_RANGE65 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8597 | 1 | MODBUS_VAR_RANGE66 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8598 | 1 | MODBUS_VAR_RANGE67 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8599 | 1 | MODBUS_VAR_RANGE68 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8600 | 1 | MODBUS_VAR_RANGE69 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8601 | 1 | MODBUS_VAR_RANGE70 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8602 | 1 | MODBUS_VAR_RANGE71 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8603 | 1 | MODBUS_VAR_RANGE72 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8604 | 1 | MODBUS_VAR_RANGE73 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8605 | 1 | MODBUS_VAR_RANGE74 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8606 | 1 | MODBUS_VAR_RANGE75 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8607 | 1 | MODBUS_VAR_RANGE76 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8608 | 1 | MODBUS_VAR_RANGE77 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8609 | 1 | MODBUS_VAR_RANGE78 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8610 | 1 | MODBUS_VAR_RANGE79 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8611 | 1 | MODBUS_VAR_RANGE80 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8612 | 1 | MODBUS_VAR_RANGE81 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8613 | 1 | MODBUS_VAR_RANGE82 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8614 | 1 | MODBUS_VAR_RANGE83 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8615 | 1 | MODBUS_VAR_RANGE84 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8616 | 1 | MODBUS_VAR_RANGE85 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8617 | 1 | MODBUS_VAR_RANGE86 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8618 | 1 | MODBUS_VAR_RANGE87 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8619 | 1 | MODBUS_VAR_RANGE88 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8620 | 1 | MODBUS_VAR_RANGE89 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8621 | 1 | MODBUS_VAR_RANGE90 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8622 | 1 | MODBUS_VAR_RANGE91 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8623 | 1 | MODBUS_VAR_RANGE92 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8624 | 1 | MODBUS_VAR_RANGE93 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8625 | 1 | MODBUS_VAR_RANGE94 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8626 | 1 | MODBUS_VAR_RANGE95 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8627 | 1 | MODBUS_VAR_RANGE96 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8628 | 1 | MODBUS_VAR_RANGE97 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8629 | 1 | MODBUS_VAR_RANGE98 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8630 | 1 | MODBUS_VAR_RANGE99 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8631 | 1 | MODBUS_VAR_RANGE100 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8632 | 1 | MODBUS_VAR_RANGE101 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8633 | 1 | MODBUS_VAR_RANGE102 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8634 | 1 | MODBUS_VAR_RANGE103 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8635 | 1 | MODBUS_VAR_RANGE104 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8636 | 1 | MODBUS_VAR_RANGE105 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8637 | 1 | MODBUS_VAR_RANGE106 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8638 | 1 | MODBUS_VAR_RANGE107 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8639 | 1 | MODBUS_VAR_RANGE108 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8640 | 1 | MODBUS_VAR_RANGE109 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8641 | 1 | MODBUS_VAR_RANGE110 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8642 | 1 | MODBUS_VAR_RANGE111 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8643 | 1 | MODBUS_VAR_RANGE112 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8644 | 1 | MODBUS_VAR_RANGE113 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8645 | 1 | MODBUS_VAR_RANGE114 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8646 | 1 | MODBUS_VAR_RANGE115 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8647 | 1 | MODBUS_VAR_RANGE116 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8648 | 1 | MODBUS_VAR_RANGE117 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8649 | 1 | MODBUS_VAR_RANGE118 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8650 | 1 | MODBUS_VAR_RANGE119 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8651 | 1 | MODBUS_VAR_RANGE120 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8652 | 1 | MODBUS_VAR_RANGE121 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8653 | 1 | MODBUS_VAR_RANGE122 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8654 | 1 | MODBUS_VAR_RANGE123 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8655 | 1 | MODBUS_VAR_RANGE124 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8656 | 1 | MODBUS_VAR_RANGE125 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8657 | 1 | MODBUS_VAR_RANGE126 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8658 | 1 | MODBUS_VAR_RANGE127 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8659 | 1 | MODBUS_VAR_RANGE128 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
8660 | 1 | MODBUS_VAR_DIGITAL_ANALOG1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8661 | 1 | MODBUS_VAR_DIGITAL_ANALOG2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8662 | 1 | MODBUS_VAR_DIGITAL_ANALOG3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8663 | 1 | MODBUS_VAR_DIGITAL_ANALOG4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8664 | 1 | MODBUS_VAR_DIGITAL_ANALOG5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8665 | 1 | MODBUS_VAR_DIGITAL_ANALOG6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8666 | 1 | MODBUS_VAR_DIGITAL_ANALOG7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8667 | 1 | MODBUS_VAR_DIGITAL_ANALOG8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8668 | 1 | MODBUS_VAR_DIGITAL_ANALOG9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8669 | 1 | MODBUS_VAR_DIGITAL_ANALOG10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8670 | 1 | MODBUS_VAR_DIGITAL_ANALOG11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8671 | 1 | MODBUS_VAR_DIGITAL_ANALOG12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8672 | 1 | MODBUS_VAR_DIGITAL_ANALOG13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8673 | 1 | MODBUS_VAR_DIGITAL_ANALOG14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8674 | 1 | MODBUS_VAR_DIGITAL_ANALOG15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8675 | 1 | MODBUS_VAR_DIGITAL_ANALOG16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8676 | 1 | MODBUS_VAR_DIGITAL_ANALOG17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8677 | 1 | MODBUS_VAR_DIGITAL_ANALOG18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8678 | 1 | MODBUS_VAR_DIGITAL_ANALOG19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8679 | 1 | MODBUS_VAR_DIGITAL_ANALOG20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8680 | 1 | MODBUS_VAR_DIGITAL_ANALOG21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8681 | 1 | MODBUS_VAR_DIGITAL_ANALOG22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8682 | 1 | MODBUS_VAR_DIGITAL_ANALOG23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8683 | 1 | MODBUS_VAR_DIGITAL_ANALOG24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8684 | 1 | MODBUS_VAR_DIGITAL_ANALOG25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8685 | 1 | MODBUS_VAR_DIGITAL_ANALOG26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8686 | 1 | MODBUS_VAR_DIGITAL_ANALOG27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8687 | 1 | MODBUS_VAR_DIGITAL_ANALOG28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8688 | 1 | MODBUS_VAR_DIGITAL_ANALOG29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8689 | 1 | MODBUS_VAR_DIGITAL_ANALOG30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8690 | 1 | MODBUS_VAR_DIGITAL_ANALOG31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8691 | 1 | MODBUS_VAR_DIGITAL_ANALOG32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8692 | 1 | MODBUS_VAR_DIGITAL_ANALOG33 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8693 | 1 | MODBUS_VAR_DIGITAL_ANALOG34 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8694 | 1 | MODBUS_VAR_DIGITAL_ANALOG35 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8695 | 1 | MODBUS_VAR_DIGITAL_ANALOG36 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8696 | 1 | MODBUS_VAR_DIGITAL_ANALOG37 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8697 | 1 | MODBUS_VAR_DIGITAL_ANALOG38 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8698 | 1 | MODBUS_VAR_DIGITAL_ANALOG39 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8699 | 1 | MODBUS_VAR_DIGITAL_ANALOG40 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8700 | 1 | MODBUS_VAR_DIGITAL_ANALOG41 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8701 | 1 | MODBUS_VAR_DIGITAL_ANALOG42 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8702 | 1 | MODBUS_VAR_DIGITAL_ANALOG43 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8703 | 1 | MODBUS_VAR_DIGITAL_ANALOG44 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8704 | 1 | MODBUS_VAR_DIGITAL_ANALOG45 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8705 | 1 | MODBUS_VAR_DIGITAL_ANALOG46 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8706 | 1 | MODBUS_VAR_DIGITAL_ANALOG47 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8707 | 1 | MODBUS_VAR_DIGITAL_ANALOG48 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8708 | 1 | MODBUS_VAR_DIGITAL_ANALOG49 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8709 | 1 | MODBUS_VAR_DIGITAL_ANALOG50 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8710 | 1 | MODBUS_VAR_DIGITAL_ANALOG51 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8711 | 1 | MODBUS_VAR_DIGITAL_ANALOG52 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8712 | 1 | MODBUS_VAR_DIGITAL_ANALOG53 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8713 | 1 | MODBUS_VAR_DIGITAL_ANALOG54 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8714 | 1 | MODBUS_VAR_DIGITAL_ANALOG55 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8715 | 1 | MODBUS_VAR_DIGITAL_ANALOG56 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8716 | 1 | MODBUS_VAR_DIGITAL_ANALOG57 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8717 | 1 | MODBUS_VAR_DIGITAL_ANALOG58 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8718 | 1 | MODBUS_VAR_DIGITAL_ANALOG59 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8719 | 1 | MODBUS_VAR_DIGITAL_ANALOG60 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8720 | 1 | MODBUS_VAR_DIGITAL_ANALOG61 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8721 | 1 | MODBUS_VAR_DIGITAL_ANALOG62 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8722 | 1 | MODBUS_VAR_DIGITAL_ANALOG63 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8723 | 1 | MODBUS_VAR_DIGITAL_ANALOG64 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8724 | 1 | MODBUS_VAR_DIGITAL_ANALOG65 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8725 | 1 | MODBUS_VAR_DIGITAL_ANALOG66 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8726 | 1 | MODBUS_VAR_DIGITAL_ANALOG67 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8727 | 1 | MODBUS_VAR_DIGITAL_ANALOG68 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8728 | 1 | MODBUS_VAR_DIGITAL_ANALOG69 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8729 | 1 | MODBUS_VAR_DIGITAL_ANALOG70 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8730 | 1 | MODBUS_VAR_DIGITAL_ANALOG71 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8731 | 1 | MODBUS_VAR_DIGITAL_ANALOG72 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8732 | 1 | MODBUS_VAR_DIGITAL_ANALOG73 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8733 | 1 | MODBUS_VAR_DIGITAL_ANALOG74 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8734 | 1 | MODBUS_VAR_DIGITAL_ANALOG75 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8735 | 1 | MODBUS_VAR_DIGITAL_ANALOG76 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8736 | 1 | MODBUS_VAR_DIGITAL_ANALOG77 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8737 | 1 | MODBUS_VAR_DIGITAL_ANALOG78 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8738 | 1 | MODBUS_VAR_DIGITAL_ANALOG79 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8739 | 1 | MODBUS_VAR_DIGITAL_ANALOG80 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8740 | 1 | MODBUS_VAR_DIGITAL_ANALOG81 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8741 | 1 | MODBUS_VAR_DIGITAL_ANALOG82 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8742 | 1 | MODBUS_VAR_DIGITAL_ANALOG83 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8743 | 1 | MODBUS_VAR_DIGITAL_ANALOG84 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8744 | 1 | MODBUS_VAR_DIGITAL_ANALOG85 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8745 | 1 | MODBUS_VAR_DIGITAL_ANALOG86 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8746 | 1 | MODBUS_VAR_DIGITAL_ANALOG87 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8747 | 1 | MODBUS_VAR_DIGITAL_ANALOG88 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8748 | 1 | MODBUS_VAR_DIGITAL_ANALOG89 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8749 | 1 | MODBUS_VAR_DIGITAL_ANALOG90 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8750 | 1 | MODBUS_VAR_DIGITAL_ANALOG91 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8751 | 1 | MODBUS_VAR_DIGITAL_ANALOG92 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8752 | 1 | MODBUS_VAR_DIGITAL_ANALOG93 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8753 | 1 | MODBUS_VAR_DIGITAL_ANALOG94 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8754 | 1 | MODBUS_VAR_DIGITAL_ANALOG95 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8755 | 1 | MODBUS_VAR_DIGITAL_ANALOG96 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8756 | 1 | MODBUS_VAR_DIGITAL_ANALOG97 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8757 | 1 | MODBUS_VAR_DIGITAL_ANALOG98 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8758 | 1 | MODBUS_VAR_DIGITAL_ANALOG99 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8759 | 1 | MODBUS_VAR_DIGITAL_ANALOG100 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8760 | 1 | MODBUS_VAR_DIGITAL_ANALOG101 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8761 | 1 | MODBUS_VAR_DIGITAL_ANALOG102 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8762 | 1 | MODBUS_VAR_DIGITAL_ANALOG103 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8763 | 1 | MODBUS_VAR_DIGITAL_ANALOG104 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8764 | 1 | MODBUS_VAR_DIGITAL_ANALOG105 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8765 | 1 | MODBUS_VAR_DIGITAL_ANALOG106 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8766 | 1 | MODBUS_VAR_DIGITAL_ANALOG107 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8767 | 1 | MODBUS_VAR_DIGITAL_ANALOG108 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8768 | 1 | MODBUS_VAR_DIGITAL_ANALOG109 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8769 | 1 | MODBUS_VAR_DIGITAL_ANALOG110 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8770 | 1 | MODBUS_VAR_DIGITAL_ANALOG111 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8771 | 1 | MODBUS_VAR_DIGITAL_ANALOG112 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8772 | 1 | MODBUS_VAR_DIGITAL_ANALOG113 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8773 | 1 | MODBUS_VAR_DIGITAL_ANALOG114 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8774 | 1 | MODBUS_VAR_DIGITAL_ANALOG115 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8775 | 1 | MODBUS_VAR_DIGITAL_ANALOG116 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8776 | 1 | MODBUS_VAR_DIGITAL_ANALOG117 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8777 | 1 | MODBUS_VAR_DIGITAL_ANALOG118 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8778 | 1 | MODBUS_VAR_DIGITAL_ANALOG119 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8779 | 1 | MODBUS_VAR_DIGITAL_ANALOG120 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8780 | 1 | MODBUS_VAR_DIGITAL_ANALOG121 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8781 | 1 | MODBUS_VAR_DIGITAL_ANALOG122 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8782 | 1 | MODBUS_VAR_DIGITAL_ANALOG123 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8783 | 1 | MODBUS_VAR_DIGITAL_ANALOG124 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8784 | 1 | MODBUS_VAR_DIGITAL_ANALOG125 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8785 | 1 | MODBUS_VAR_DIGITAL_ANALOG126 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8786 | 1 | MODBUS_VAR_DIGITAL_ANALOG127 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
8787 | 1 | MODBUS_VAR_DIGITAL_ANALOG128 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 - digital , 1 - analog
15808 | 21 | MODBUS_SCHEDULE_LIST1 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | 15808 - 15817 Full Lable 21 characters 10.5 registers 15818 - 15822 Lable 9 characters 4.5 registers 15823 High Byte-> Output(ON/OFF) Low Byte-> Auto/Manual 15824 High Byte-> Holiday1(ON/OFF) Low Byte-> Holiday2(ON/OFF) 15825 unused 15826 3bytes (That tells you which Holiday to fill in)
15829 | 21 | MODBUS_SCHEDULE_LIST2 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15850 | 21 | MODBUS_SCHEDULE_LIST3 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15871 | 21 | MODBUS_SCHEDULE_LIST4 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15892 | 21 | MODBUS_SCHEDULE_LIST5 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15913 | 21 | MODBUS_SCHEDULE_LIST6 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15934 | 21 | MODBUS_SCHEDULE_LIST7 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
15955 | 21 | MODBUS_SCHEDULE_LIST8 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
32044 | 72 | MODBUS_SCHEDULE_LIST1_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday example: Monday 32044 - 32051 8 registers ON_1 32044 e.g. Value is 0x0607 Means 07:06 OFF_1 32045 e.g. Value is 0x1110 Means 16:17 ON_2 32046 OFF_2 32047 ON_3 32048 OFF_3 32049 ON_4 32050 OFF_4 32051 The rest is the same as Monday TuesDay 32052 - 32059 Wednesday 32060 - 32067 Thursday 32068 - 32075 Friday 32076 - 32083 Suturday 32084 - 32091 Sunday 32092 - 32099 Holiday1 32100 - 32107 Holiday2 32108 - 32115
32116 | 72 | MODBUS_SCHEDULE_LIST2_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32116 … Same as above mentioned
32188 | 72 | MODBUS_SCHEDULE_LIST3_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32188 Same as above mentioned
32260 | 72 | MODBUS_SCHEDULE_LIST4_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32260 Same as above mentioned
32332 | 72 | MODBUS_SCHEDULE_LIST5_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32332 Same as above mentioned
32404 | 72 | MODBUS_SCHEDULE_LIST6_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32404 Same as above mentioned
32476 | 72 | MODBUS_SCHEDULE_LIST7_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32476 Same as above mentioned
32548 | 72 | MODBUS_SCHEDULE_LIST8_TIME | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Monday ON1 32548 Same as above mentioned
33201 | 36 | MODBUS_SCHEDULE_FLAG1 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | example: Hi byte -- FLAG of Event1,Event3,Event5,Event7 Low byte -- Flag of Event2,Eevet4,Event6,Event8 1: ON 0:OFF 0xff:unused
33237 | 36 | MODBUS_SCHEDULE_FLAG2 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33273 | 36 | MODBUS_SCHEDULE_FLAG3 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33309 | 36 | MODBUS_SCHEDULE_FLAG4 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33345 | 36 | MODBUS_SCHEDULE_FLAG5 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33381 | 36 | MODBUS_SCHEDULE_FLAG6 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33417 | 36 | MODBUS_SCHEDULE_FLAG7 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned
33453 | 36 | MODBUS_SCHEDULE_FLAG8 | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Same as above mentioned

## TSTAT8&7
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | Serial Number - 4 byte value. Read-only
4 | 2 | MODBUS_VERSION_NUMBER_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Software Version – 2 byte value. Read-only
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | ADDRESS. Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Product Model. This is a read-only register that is used by the microcontroller to determine the product
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | [INVALID_DATA]
9 | 1 | MODBUS_PIC_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIC firmware version
10 | 1 | MODBUS_HUM_PIC_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIC version of Humidity module
11 | 1 | MODBUS_ADDRESS_PLUG_N_PLAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
14 | 1 | MODBUS_BASE_ADDRESS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | MODBUS_BASE_ADDRESS
15 | 1 | MODBUS_BAUDRATE | 03 Read Holding Registers | 16 Bit Unsigned Integer | baudrate 0:9600 1:19200 4:115200
16 | 1 | MODBUS_UPDATE_STATUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Firmware Update Register, used to show the status of firmware updates.Writing 143 sets the config back to out of the box except for Modbus ID and baud rate. Write 159 to fix the current config as the user defaults, this is done automatically by T3000 any
20 | 1 | MODBUS_HARDWARE_INFORMATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Options Register, starting with LSB: Bit0=Clock present or not, Bit1 = Humidity present or not, Bit2 = C02 Sensor, Bit3=CO sensor, Bit4 = Motion Sensor
21 | 1 | MODBUS_PROTOCOL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0:modbud 1:bacnet
23 | 2 | MODBUS_MAX_MASTER | 03_06 Read Holding Registers | 32 Bit Unsigned Integer | max master number for bacnet station
101 | 1 | MODBUS_COOL_HEAT_MODE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | COOL_HEAT_MODE, heating or cooling mode. 0=none, 1=cooling, 2=heating.
102 | 1 | MODBUS_MODE_OPERATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | MODE_OPERATION, heating or cooling state: 0-7 = coasting, cooling 1,2,3, heating 1,2,3
103 | 1 | MODBUS_SEQUENCE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | SEQUENCE , 0 = internal test sequence, outputs slowly cycle on/off or ramp up & down. 1 = normal, operation according to the output tables.
104 | 1 | MODBUS_DEGC_OR_F | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | DEGC_OR_F, engineering units, Deg C = 0, Deg F = 1
105 | 1 | MODBUS_FAN_MODE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | numer of fan speeds or system modes,.. Single speed = 1 up to three speed fan = 3
106 | 1 | MODBUS_POWERUP_MODE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | COOL_HEAT_MODE, heating or cooling mode. 0=none, 1=cooling, 2=heating.
107 | 1 | MODBUS_AUTO_ONLY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | MODE_OPERATION, heating or cooling state: 0-7 = coasting, cooling 1,2,3, heating 1,2,3
108 | 1 | MODBUS_FACTORY_DEFAULTS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Write 1 to register 108 - resets the unit to latest factory defaults. (same as writing Writing 143 to register 16)
109 | 1 | MODBUS_INFO_BYTE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Occupied/Unoccupied Mode: 26=unoccupied, 27=occupied - controlled by Tstat when schedules are active
111 | 1 | MODBUS_OVERRIDE_TIMER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Unoccupied Override Timer, Ort. 0=disabled, >0=number of minutes manual override is allowed
112 | 1 | MODBUS_OVERRIDE_TIMER_LEFT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
113 | 1 | MODBUS_HEAT_COOL_CONFIG | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
114 | 1 | MODBUS_TIMER_ON | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Period timer ON time.
115 | 1 | MODBUS_TIMER_OFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Period timer OFF time.
116 | 1 | MODBUS_TIMER_UNITS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Period timer units. 0, second; 1, minute; 2, hour.
117 | 1 | MODBUS_DEAD_MASTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Dead master. The Tstat will go to occupied mode automatically if there is no serial communications for a user defined period of time, for example if the register is set to 10 the thermostat will go to ocupied mode if there are no communications for a peri
118 | 1 | MODBUS_SYSTEM_TIME_FORMAT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Time format. 0 = 12hours,1 = 24hours, in TSTAT6, it always 24h
119 | 1 | MODBUS_FREE_COOL_CONFIG | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | free cool configure byte
120 | 1 | MODBUS_RS485_MODE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | RS485 mode/wireless selection, user can not change this register. Factory set only.
121 | 1 | MODBUS_TEMPRATURE_CHIP | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | TEMPERATURE reading in DegC or F from the sensor used in the control loop PI1 which is configured in register 111. This can be the internal sensor, external, or an average of the two. Writing a temperature value to this register will calibrate the curren
122 | 1 | MODBUS_ANALOG1_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ANALOG INPUT1 RANGE. 0 = raw data, 1 = thermistor, 2 = %, 3 = ON/OFF, 4 = N/A, 5 = OFF/ON
123 | 1 | MODBUS_ANALOG2_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ANALOG INPUT2 RANGE. 0 = raw data, 1 = thermistor, 2 = %, 3 = ON/OFF, 4 = N/A, 5 = OFF/ON
124 | 1 | MODBUS_ANALOG3_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ANALOG INPUT3 RANGE. 0 = raw data, 1 = thermistor, 2 = %, 3 = ON/OFF, 4 = N/A, 5 = OFF/ON
125 | 1 | MODBUS_ANALOG4_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ANALOG INPUT4 RANGE. 0 = raw data, 1 = thermistor, 2 = %, 3 = ON/OFF, 4 = N/A, 5 = OFF/ON
126 | 1 | MODBUS_ANALOG5_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ANALOG INPUT5 RANGE. 0 = raw data, 1 = thermistor, 2 = %, 3 = ON/OFF, 4 = N/A, 5 = OFF/ON
127 | 1 | MODBUS_ANALOG6_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ANALOG INPUT6 RANGE. 0 = raw data, 1 = thermistor, 2 = %, 3 = ON/OFF, 4 = N/A, 5 = OFF/ON
128 | 1 | MODBUS_ANALOG7_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ANALOG INPUT7 RANGE. 0 = raw data, 1 = thermistor, 2 = %, 3 = ON/OFF, 4 = N/A, 5 = OFF/ON
129 | 1 | MODBUS_ANALOG8_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ANALOG INPUT8 RANGE. 0 = raw data, 1 = thermistor, 2 = %, 3 = ON/OFF, 4 = N/A, 5 = OFF/ON
130 | 1 | MODBUS_INTERNAL_THERMISTOR | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | Internal Thermistor Sensor - Shows the filtered, calibrated value of the internal thermistor sensor
131 | 1 | MODBUS_ANALOG_INPUT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input1 value
132 | 1 | MODBUS_ANALOG_INPUT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input2 value
133 | 1 | MODBUS_ANALOG_INPUT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input3 value
134 | 1 | MODBUS_ANALOG_INPUT4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input4 value
135 | 1 | MODBUS_ANALOG_INPUT5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input5 value
136 | 1 | MODBUS_ANALOG_INPUT6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input6 value
137 | 1 | MODBUS_ANALOG_INPUT7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input7 value
138 | 1 | MODBUS_ANALOG_INPUT8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input8 value
139 | 1 | MODBUS_EXTERNAL_SENSOR1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | co2 ppm(optional)
140 | 1 | MODBUS_EXTERNAL_SENSOR2 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | humidity % (optional)
141 | 1 | MODBUS_INPUT_MANU_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Auto Manual mode for inputs, bit 0 = input1, bit1 = input2 and so on. In manual mode you can write to the input registers 311 & 312 for debugging & commissioning.
142 | 1 | MODBUS_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Temperature sensor filter, FIL, weighted average of stored value to new raw value
143 | 1 | MODBUS_INPUT1_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input1 filer
144 | 1 | MODBUS_INPUT2_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input2 filer
145 | 1 | MODBUS_INPUT3_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input3 filer
146 | 1 | MODBUS_INPUT4_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input4 filer
147 | 1 | MODBUS_INPUT5_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input5 filer
148 | 1 | MODBUS_INPUT6_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input6 filer
149 | 1 | MODBUS_INPUT7_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input7 filer
150 | 1 | MODBUS_INPUT8_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input8 filer
151 | 1 | MODBUS_EX_SENSOR1_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | sensor1 filter?
152 | 1 | MODBUS_EX_SENSOR2_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | sensor2 filter?
153 | 1 | MODBUS_CALIBRATION_TERM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CALIBRATION, this is the calibration factor for the internal sensor, normally maintained by the tstat.
154 | 1 | MODBUS_CALIBRATION_INTERNAL_THERMISTOR | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | Calibration for the internal thermistor - internally managed offset for the internal temp sensor value
155 | 1 | MODBUS_CALIBRATION_ANALOG1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Calibration for analog input1
156 | 1 | MODBUS_CALIBRATION_ANALOG2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Calibration for analog input2
157 | 1 | MODBUS_CALIBRATION_ANALOG3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Calibration for analog input3
158 | 1 | MODBUS_CALIBRATION_ANALOG4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Calibration for analog input4
159 | 1 | MODBUS_CALIBRATION_ANALOG5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Calibration for analog input5
160 | 1 | MODBUS_CALIBRATION_ANALOG6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Calibration for analog input6
161 | 1 | MODBUS_CALIBRATION_ANALOG7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Calibration for analog input7
162 | 1 | MODBUS_CALIBRATION_ANALOG8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Calibration for analog input8
167 | 1 | MODBUS_ANALOG1_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input1 function selection. 0, normal; 1, freeze protect sensor input; 2, occupancy sensor input; 3, sweep off mode; 4, clock mode; 5, change over mode.
168 | 1 | MODBUS_ANALOG2_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog input2 function selection. 0, normal; 1, freeze protect sensor input; 2, occupancy sensor input; 3, sweep off mode; 4, clock mode; 5, change over mode.
169 | 1 | MODBUS_ANALOG3_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Analog input3 function selection. 0, normal; 1, freeze protect sensor input; 2, occupancy sensor input; 3, sweep off mode; 4, clock mode; 5, change over mode.
170 | 1 | MODBUS_ANALOG4_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Analog input4 function selection. 0, normal; 1, freeze protect sensor input; 2, occupancy sensor input; 3, sweep off mode; 4, clock mode; 5, change over mode.
171 | 1 | MODBUS_ANALOG5_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Analog input5 function selection. 0, normal; 1, freeze protect sensor input; 2, occupancy sensor input; 3, sweep off mode; 4, clock mode; 5, change over mode.
172 | 1 | MODBUS_ANALOG6_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Analog input6 function selection. 0, normal; 1, freeze protect sensor input; 2, occupancy sensor input; 3, sweep off mode; 4, clock mode; 5, change over mode.
173 | 1 | MODBUS_ANALOG7_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Analog input7 function selection. 0, normal; 1, freeze protect sensor input; 2, occupancy sensor input; 3, sweep off mode; 4, clock mode; 5, change over mode.
174 | 1 | MODBUS_ANALOG8_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Analog input8 function selection. 0, normal; 1, freeze protect sensor input; 2, occupancy sensor input; 3, sweep off mode; 4, clock mode; 5, change over mode.
175 | 1 | MODBUS_TABLE1_ZERO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 1 - 0.0V value Sensor value that corresponds to 0.0V
176 | 1 | MODBUS_TABLE1_HALFONE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 1 - 0.5V value Sensor value that corresponds to 0.5V
177 | 1 | MODBUS_TABLE1_ONE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 1 - 1.0V value Sensor value that corresponds to 1.0V
178 | 1 | MODBUS_TABLE1_HALFTWO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 1 - 1.5V value Sensor value that corresponds to 1.5V
179 | 1 | MODBUS_TABLE1_TWO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 1 - 2.0V value Sensor value that corresponds to 2.0V
180 | 1 | MODBUS_TABLE1_HALFTHREE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 1 - 2.5V value Sensor value that corresponds to 2.5V
181 | 1 | MODBUS_TABLE1_THREE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 1 - 3.0V value Sensor value that corresponds to 3.0V
182 | 1 | MODBUS_TABLE1_HALFFOUR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 1 - 3.5V value Sensor value that corresponds to 3.5V
183 | 1 | MODBUS_TABLE1_FOUR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 1 - 4.0V value Sensor value that corresponds to 4.0V
184 | 1 | MODBUS_TABLE1_HALFFIVE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 1 - 4.5V value Sensor value that corresponds to 4.5V
185 | 1 | MODBUS_TABLE1_FIVE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 1 - 5.0V value Sensor value that corresponds to 5.0V
186 | 1 | MODBUS_TABLE2_ZERO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 2 - 0.0V value Sensor value that corresponds to 0.0V
187 | 1 | MODBUS_TABLE2_HALFONE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 2 - 0.5V value Sensor value that corresponds to 0.5V
188 | 1 | MODBUS_TABLE2_ONE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 2 - 1.0V value Sensor value that corresponds to 1.0V
189 | 1 | MODBUS_TABLE2_HALFTWO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 2 - 1.5V value Sensor value that corresponds to 1.5V
190 | 1 | MODBUS_TABLE2_TWO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 2 - 2.0V value Sensor value that corresponds to 2.0V
191 | 1 | MODBUS_TABLE2_HALFTHREE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 2 - 2.5V value Sensor value that corresponds to 2.5V
192 | 1 | MODBUS_TABLE2_THREE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 2 - 3.0V value Sensor value that corresponds to 3.0V
193 | 1 | MODBUS_TABLE2_HALFFOUR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 2 - 3.5V value Sensor value that corresponds to 3.5V
194 | 1 | MODBUS_TABLE2_FOUR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 2 - 4.0V value Sensor value that corresponds to 4.0V
195 | 1 | MODBUS_TABLE2_HALFFIVE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 2 - 4.5V value Sensor value that corresponds to 4.5V
196 | 1 | MODBUS_TABLE2_FIVE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lookup Table 2 - 5.0V value Sensor value that corresponds to 5.0V
202 | 1 | MODBUS_MODE_OUTPUT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Determine the output1 mode. 0, ON/OFF mode; 1, floating valve for cooling; 2, floating valve for heating 3, PWM
203 | 1 | MODBUS_MODE_OUTPUT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Determine the output2 mode. 0, ON/OFF mode; 1, floating valve for cooling; 2, floating valve for heating 3, PWM
204 | 1 | MODBUS_MODE_OUTPUT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Determine the output3 mode. 0, ON/OFF mode; 1, floating valve for cooling; 2, floating valve for heating 3, PWM
205 | 1 | MODBUS_MODE_OUTPUT4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Determine the output4 mode. 0, ON/OFF mode; 1, floating valve for cooling; 2, floating valve for heating 3, PWM
206 | 1 | MODBUS_MODE_OUTPUT5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Determine the output5 mode. 0, ON/OFF mode; 1, floating valve for cooling; 2, floating valve for heating 3, PWM
207 | 1 | MODBUS_OUTPUT1_SCALE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog Output1 range - 0=On/Off, 1=0-10V, 2=0-5V, 3=2-10V, 4= 10-0V
208 | 1 | MODBUS_OUTPUT2_SCALE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog Output2 range - 0=On/Off, 1=0-10V, 2=0-5V, 3=2-10V, 4= 10-0V
209 | 1 | MODBUS_DIGITAL_OUTPUT_STATUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output1 to 5, bit 0 thru 4 = relay 1 thru 5.
210 | 1 | MODBUS_COOLING_VALVE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output6, Analog output1, a number from 0-1000 representing 0% (closed) to 100% (open). When Range = On/Off mode, On=1000, Off=0.
211 | 1 | MODBUS_HEATING_VALVE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output7, Analog output2, a number from 0-1000 representing 0% (closed) to 100% (open). When Range = On/Off mode, On=1000, Off=0.
212 | 1 | MODBUS_DAC_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | DAC_OFFSET , Calibration data for the 0-10VDC signal, internal variable maintained by tstat
213 | 1 | MODBUS_OUTPUT1_DELAY_OFF_TO_ON | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output1 Relay1_delay_OFF_TO_ON – delay time for output1 going from OFF to ON (sec)
214 | 1 | MODBUS_OUTPUT2_DELAY_OFF_TO_ON | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output2 Relay2_delay_OFF_TO_ON – delay time for output2 going from OFF to ON (sec)
215 | 1 | MODBUS_OUTPUT3_DELAY_OFF_TO_ON | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output3 Relay3_delay_OFF_TO_ON – delay time for output3 going from OFF to ON (sec)
216 | 1 | MODBUS_OUTPUT4_DELAY_OFF_TO_ON | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output4 Relay4_delay_OFF_TO_ON – delay time for output4 going from OFF to ON (sec)
217 | 1 | MODBUS_OUTPUT5_DELAY_OFF_TO_ON | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output5 Relay5_delay_OFF_TO_ON – delay time for output5 going from OFF to ON (sec)
218 | 1 | MODBUS_OUTPUT6_DELAY_OFF_TO_ON | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Output6 delay_OFF_TO_ON – delay time for output4 going from OFF to ON (sec)
219 | 1 | MODBUS_OUTPUT7_DELAY_OFF_TO_ON | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Output7 delay_OFF_TO_ON – delay time for output5 going from OFF to ON (sec)
220 | 1 | MODBUS_DELAY1_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output 1 current time left from OFF to ON
221 | 1 | MODBUS_DELAY2_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output 2 current time left from OFF to ON
222 | 1 | MODBUS_DELAY3_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output 3 current time left from OFF to ON
223 | 1 | MODBUS_DELAY4_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output 4 current time left from OFF to ON
224 | 1 | MODBUS_DELAY5_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output 5 current time left from OFF to ON
225 | 1 | MODBUS_DELAY6_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | (reserved)output 6 current time left from OFF to ON
226 | 1 | MODBUS_DELAY7_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | (reserved)output 7 current time left from OFF to ON
227 | 1 | MODBUS_OUTPUT1_DELAY_ON_TO_OFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output1 Relay1_delay_ON_TO_OFF – delay time for output1 going from ON to OFF (sec)
228 | 1 | MODBUS_OUTPUT2_DELAY_ON_TO_OFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output2 Relay2_delay_ON_TO_OFF – delay time for output2 going from ON to OFF (sec)
229 | 1 | MODBUS_OUTPUT3_DELAY_ON_TO_OFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output3 Relay3_delay_ON_TO_OFF – delay time for output3 going from ON to OFF (sec)
230 | 1 | MODBUS_OUTPUT4_DELAY_ON_TO_OFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output4 Relay4_delay_ON_TO_OFF – delay time for output4 going from ON to OFF(sec)
231 | 1 | MODBUS_OUTPUT5_DELAY_ON_TO_OFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output5 Relay5_delay_ON_TO_OFF – delay time for output5 going from ON to OFF(sec)
232 | 1 | MODBUS_OUTPUT6_DELAY_ON_TO_OFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Output6_delay_ON_TO_OFF – delay time for output4 going from ON to OFF(sec)
233 | 1 | MODBUS_OUTPUT7_DELAY_ON_TO_OFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Output7_delay_ON_TO_OFF – delay time for output5 going from ON to OFF (sec)
234 | 1 | MODBUS_DELAY1_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output 1 current time left from ON to OFF
235 | 1 | MODBUS_DELAY2_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output 2 current time left from ON to OFF
236 | 1 | MODBUS_DELAY3_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output 3 current time left from ON to OFF
237 | 1 | MODBUS_DELAY4_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output 4 current time left from ON to OFF
238 | 1 | MODBUS_DELAY5_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output 5 current time left from ON to OFF
239 | 1 | MODBUS_DELAY6_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | (reserved)output 6 current time left from ON to OFF
240 | 1 | MODBUS_DELAY7_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | (reserved)output 7 current time left from ON to OFF
241 | 1 | MODBUS_CYCLING_DELAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
242 | 1 | MODBUS_CHANGOVER_DELAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
243 | 1 | MODBUS_VALVE_TRAVEL_TIME | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Valve travel time. The time of the valve travel from one end to another end. The units is second.
244 | 1 | MODBUS_VALVE_PERCENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Valve percent. Show the valve opened how much percent. READ ONLY
245 | 1 | MODBUS_INTERLOCK_OUTPUT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
246 | 1 | MODBUS_INTERLOCK_OUTPUT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
247 | 1 | MODBUS_INTERLOCK_OUTPUT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
248 | 1 | MODBUS_INTERLOCK_OUTPUT4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
249 | 1 | MODBUS_INTERLOCK_OUTPUT5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
250 | 1 | MODBUS_INTERLOCK_OUTPUT6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
251 | 1 | MODBUS_INTERLOCK_OUTPUT7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
252 | 1 | MODBUS_FREEZE_DELAY_ON | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
253 | 1 | MODBUS_FREEZE_DELAY_OFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Delay to close. The duration the heating valve open. The units is minute.
254 | 1 | MODBUS_OUTPUT_MANU_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Auto Manual mode for outputs, bit 0 = relay1, bit1 = relay2… bit 5 = (out6) analogout1, bit6 = (out7) analogout2. In manual mode you can write to the output registers for debugging or from an external master to override the local PID logic.
255 | 1 | MODBUS_MANU_RELAY1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Not used
256 | 1 | MODBUS_MANU_RELAY2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Not used
257 | 1 | MODBUS_MANU_RELAY3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Not used
258 | 1 | MODBUS_MANU_RELAY4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Not used
259 | 1 | MODBUS_MANU_RELAY5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Not used
260 | 1 | MODBUS_MANUAL_AO1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Not used
261 | 1 | MODBUS_MANUAL_AO2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Not used
262 | 1 | MODBUS_DEADMASTER_AUTO_MANUAL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
263 | 1 | MODBUS_DEADMASTER_OUTPUT_STATE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
264 | 1 | MODBUS_DEADMASTER_COOL_OUTPUT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog Output1 goes to this value when DEADMASTER_MODE = 2 (active), 0-1000
265 | 1 | MODBUS_DEADMASTER_HEAT_OUTPUT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Analog Output2 goes to this value when DEADMASTER_MODE = 2 (active), 0-1000
266 | 1 | MODBUS_OUTPUT1_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
267 | 1 | MODBUS_OUTPUT2_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output2 function setting (see above)
268 | 1 | MODBUS_OUTPUT3_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output3 function setting (see above)
269 | 1 | MODBUS_OUTPUT4_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output4 function setting (see above)
270 | 1 | MODBUS_OUTPUT5_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output5 function setting (see above)
271 | 1 | MODBUS_OUTPUT6_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Output6 function setting (see above)
272 | 1 | MODBUS_OUTPUT7_FUNCTION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (future)Output7 function setting (see above)
273 | 1 | MODBUS_FAN_SPEED | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
274 | 1 | MODBUS_PID_OUTPUT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output 1 PID Interlock 0 = PID1, can assign each output to either PID1 or 2, the max or the min of the two PIDS
275 | 1 | MODBUS_PID_OUTPUT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output 2 PID Interlock 1 = PID2
276 | 1 | MODBUS_PID_OUTPUT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output 3 PID Interlock 2 = Maximum of PID1 and PID2
277 | 1 | MODBUS_PID_OUTPUT4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output 4 PID Interlock 3 = Minimum of PID1 and PID2
278 | 1 | MODBUS_PID_OUTPUT5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output 5 PID Interlock
279 | 1 | MODBUS_PID_OUTPUT6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output 6 PID Interlock
280 | 1 | MODBUS_PID_OUTPUT7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Output 7 PID Interlock
281 | 1 | MODBUS_UNIVERSAL_OUTPUT_BEGIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 Output table- Coasting
282 | 1 | MODBUS_UNIVERSAL_OUTPUT_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 Output table- Cooling1
283 | 1 | MODBUS_UNIVERSAL_OUTPUT_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 Output table- Cooling2
284 | 1 | MODBUS_UNIVERSAL_OUTPUT_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 Output table- Cooling3
285 | 1 | MODBUS_UNIVERSAL_OUTPUT_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 Output - Heating1
286 | 1 | MODBUS_UNIVERSAL_OUTPUT_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 Output - Heating2
287 | 1 | MODBUS_UNIVERSAL_OUTPUT_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 Output - Heating3
288 | 1 | MODBUS_FAN0_OPER_TABLE_COAST | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN0_OPERATION_TABLE_COAST
289 | 1 | MODBUS_FAN0_OPER_TABLE_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN0_OPERATION_TABLE_COOL1
290 | 1 | MODBUS_FAN0_OPER_TABLE_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN0_OPERATION_TABLE_COOL2
291 | 1 | MODBUS_FAN0_OPER_TABLE_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN0_OPERATION_TABLE_COOL3
292 | 1 | MODBUS_FAN0_OPER_TABLE_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN0_OPERATION_TABLE_HEAT1
293 | 1 | MODBUS_FAN0_OPER_TABLE_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN0_OPERATION_TABLE_HEAT2
294 | 1 | MODBUS_FAN0_OPER_TABLE_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN0_OPERATION_TABLE_HEAT3
295 | 1 | MODBUS_FAN1_OPER_TABLE_COAST | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN1_OPERATION_TABLE_COAST
296 | 1 | MODBUS_FAN1_OPER_TABLE_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN1_OPERATION_TABLE_COOL1
297 | 1 | MODBUS_FAN1_OPER_TABLE_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN1_OPERATION_TABLE_COOL2
298 | 1 | MODBUS_FAN1_OPER_TABLE_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN1_OPERATION_TABLE_COOL3
299 | 1 | MODBUS_FAN1_OPER_TABLE_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN1_OPERATION_TABLE_HEAT1
300 | 1 | MODBUS_FAN1_OPER_TABLE_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN1_OPERATION_TABLE_HEAT2
301 | 1 | MODBUS_FAN1_OPER_TABLE_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN1_OPERATION_TABLE_HEAT3
302 | 1 | MODBUS_FAN2_OPER_TABLE_COAST | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN2_OPERATION_TABLE_COAST
303 | 1 | MODBUS_FAN2_OPER_TABLE_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN2_OPERATION_TABLE_COOL1
304 | 1 | MODBUS_FAN2_OPER_TABLE_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN2_OPERATION_TABLE_COOL2
305 | 1 | MODBUS_FAN2_OPER_TABLE_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN2_OPERATION_TABLE_COOL3
306 | 1 | MODBUS_FAN2_OPER_TABLE_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN2_OPERATION_TABLE_HEAT1
307 | 1 | MODBUS_FAN2_OPER_TABLE_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN2_OPERATION_TABLE_HEAT2
308 | 1 | MODBUS_FAN2_OPER_TABLE_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN2_OPERATION_TABLE_HEAT3
309 | 1 | MODBUS_FAN3_OPER_TABLE_COAST | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN3_OPERATION_TABLE_COAST
310 | 1 | MODBUS_FAN3_OPER_TABLE_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN3_OPERATION_TABLE_COOL1
311 | 1 | MODBUS_FAN3_OPER_TABLE_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN3_OPERATION_TABLE_COOL2
312 | 1 | MODBUS_FAN3_OPER_TABLE_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN3_OPERATION_TABLE_COOL3
313 | 1 | MODBUS_FAN3_OPER_TABLE_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN3_OPERATION_TABLE_HEAT1
314 | 1 | MODBUS_FAN3_OPER_TABLE_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN3_OPERATION_TABLE_HEAT2
315 | 1 | MODBUS_FAN3_OPER_TABLE_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FAN3_OPERATION_TABLE_HEAT3
316 | 1 | MODBUS_FANAUT_OPER_TABLE_COAST | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FANAUT_OPERATION_TABLE_COAST
317 | 1 | MODBUS_FANAUT_OPER_TABLE_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FANAUT_OPERATION_TABLE_COOL1
318 | 1 | MODBUS_FANAUT_OPER_TABLE_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FANAUT_OPERATION_TABLE_COOL2
319 | 1 | MODBUS_FANAUT_OPER_TABLE_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FANAUT_OPERATION_TABLE_COOL3
320 | 1 | MODBUS_FANAUT_OPER_TABLE_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FANAUT_OPERATION_TABLE_HEAT1
321 | 1 | MODBUS_FANAUT_OPER_TABLE_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FANAUT_OPERATION_TABLE_HEAT2
322 | 1 | MODBUS_FANAUT_OPER_TABLE_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | FANAUT_OPERATION_TABLE_HEAT3
323 | 1 | MODBUS_VALVE_OPERATION_TABLE_BEGIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VALVE_OPER_TABLE_COAST, Analog output state for each of the 7 modes of operation
324 | 1 | MODBUS_VALVE_OPER_TABLE_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VALVE_OPER_TABLE_COOLING1
325 | 1 | MODBUS_VALVE_OPER_TABLE_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VALVE_OPER_TABLE_COOLING2
326 | 1 | MODBUS_VALVE_OPER_TABLE_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VALVE_OPER_TABLE_COOLING3
327 | 1 | MODBUS_VALVE_OPER_TABLE_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VALVE_OPER_TABLE_HEATING1
328 | 1 | MODBUS_VALVE_OPER_TABLE_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VALVE_OPER_TABLE_HEATING2
329 | 1 | MODBUS_VALVE_OPER_TABLE_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | VALVE_OPER_TABLE_HEATING3
330 | 1 | MODBUS_HEAT_UNIVERSAL_TABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Number of Universal Heating Stages (Max heat+cool = 6)
331 | 1 | MODBUS_COOL_UNIVERSAL_TABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Number of Universal Cooling Stages (Max heat + Cool = 6)
332 | 1 | MODBUS_HEAT_ORIGINAL_TABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Number of Heating Stages in Original Table - (Maximum # of total heating and cooling states is 6)
333 | 1 | MODBUS_COOL_ORIGINAL_TABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Number of Cooling Stages in Original Table - (Maximum # of total heating and cooling states is 6)
334 | 1 | MODBUS_VALVE_OFF_TABLE_COAST | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID1 VALVE OFF TABLE COASTING
335 | 1 | MODBUS_VALVE_OFF_TABLE_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID1 VALVE OFF TABLE COOLING1
336 | 1 | MODBUS_VALVE_OFF_TABLE_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID1 VALVE OFF TABLE COOLING2
337 | 1 | MODBUS_VALVE_OFF_TABLE_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID1 VALVE OFF TABLE COOLING3
338 | 1 | MODBUS_VALVE_OFF_TABLE_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID1 VALVE OFF TABLE HEATING1
339 | 1 | MODBUS_VALVE_OFF_TABLE_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID1 VALVE OFF TABLE HEATING2
340 | 1 | MODBUS_VALVE_OFF_TABLE_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID1 VALVE OFF TABLE HEATING3
341 | 1 | MODBUS_DEFAULT_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Default occupied setpoint.
345 | 1 | MODBUS_DAY_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (Day)Occupied setpoint
346 | 1 | MODBUS_DAY_COOLING_DEADBAND | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (Day)Occupied cooling setpoint dead band, offset from setpoint for cooling to begin. Units are 0.1 deg.
347 | 1 | MODBUS_DAY_HEATING_DEADBAND | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (Day)Occupied heating setpoint dead band, offset from setpoint for heating to begin. Units are 0.1 deg.
348 | 1 | MODBUS_DAY_COOLING_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (Day)Occupied cooling setpoint (day cooling setpoint)
349 | 1 | MODBUS_DAY_HEATING_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (Day)Occupied heating setpoint (day heating setpoint)
350 | 1 | MODBUS_NIGHT_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (Night)Unoccupied setpoint
352 | 1 | MODBUS_NIGHT_HEATING_DEADBAND | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (Night)Unoccupied heating setpoint dead band, heating deadband for the night (OFF) mode. Units of 1 deg.
353 | 1 | MODBUS_NIGHT_COOLING_DEADBAND | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (Night)Unoccupied cooling setpoint dead band, cooling deadband for the night (OFF) mode. Units of 1 deg.
354 | 1 | MODBUS_NIGHT_HEATING_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (Night)Unoccupied heating setpoint
355 | 1 | MODBUS_NIGHT_COOLING_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (Night)Unoccupied cooling setpoint
358 | 1 | MODBUS_UNIVERSAL_NIGHTSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 Unoccupied (OFF) Setpoint
359 | 1 | MODBUS_UNIVERSAL_SET | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | PID2 Occupied Setpoint
360 | 1 | MODBUS_UNIVERSAL_DB_HI | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | PID2 Heating Deadband, TBD: can write to either deadband or to setpoint
361 | 1 | MODBUS_UNIVERSAL_DB_LO | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | PID2 Cooling Deadband, TBD: can write to either deadband or to setpoint
362 | 1 | MODBUS_ECOMONY_COOLING_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | economy mode cooling setpoint
363 | 1 | MODBUS_ECOMONY_HEATING_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | economy mode heating setpoint
364 | 1 | MODBUS_POWERUP_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | POWERUP_SETPOINT , setpoint on power up
365 | 1 | MODBUS_MAX_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | MAX_SETPOINT, Setpoint high, the highest setpoint a user will be able to set from the keypad.
366 | 1 | MODBUS_MIN_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | MIN_SETPOINT, Setpoint Low, the lowest setpoint a user will be able to set from the keypad.
373 | 1 | MODBUS_SETPOINT_INCREASE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Setpoint increment on the display each time the user hits the up/down buttons. Units are 0.1Deg, 10 = 1Deg and so on.
380 | 1 | MODBUS_SETPOINT_UNLIMIT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0: setpoint limited by max sp and min sp 1:setpoint unlimited
382 | 1 | MODBUS_TEMP_SELECT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Sensor to be used for the PID calculations, 1= external sensor analog input 1, 2 = internal thermistor, 3 = average the internal thermistor and analog input1
383 | 1 | MODBUS_INPUT1_SELECT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Universal PID(PID2) input select, 0=none, 1=analog_in1, 2=analog_in2, 3=analog_in3, 4=analog_in4,5=analog_in5,6=analog_in6,7=analog_in7,8=analog_in8,9= humidity 10= co2
384 | 1 | MODBUS_COOLING_PID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PID1, current PI calculation for PID number 1 (PID2 is in register 240)
385 | 1 | MODBUS_COOLING_PTERM | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | COOLING PTERM , proportional term for PI calculation
386 | 1 | MODBUS_COOLING_ITERM | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | COOLING ITEM
387 | 1 | MODBUS_UNIVERSAL_PTERM | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | PID2 P term
388 | 1 | MODBUS_UNIVERSAL_ITERM | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | PID2 I term
389 | 1 | MODBUS_PID_UNIVERSAL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PID2, the current value of PID number 2
390 | 1 | MODBUS_UNITS1_HIGH | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID1 Units High byte - Upper 2 bytes of the PID1 units in ASCII
391 | 1 | MODBUS_UNITS1_LOW | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID1 Units Low byte - Lower 2 bytes of the PID1 units in ASCII
392 | 1 | MODBUS_UNITS2_HIGH | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 Units High byte - Upper 2 bytes of the PID2 units in ASCII
393 | 1 | MODBUS_UNITS2_LOW | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 Units Low byte - Lower 2 bytes of the PID2 units in ASCII
394 | 1 | MODBUS_PID2_MODE_OPERATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PID2 heating or cooling state derived from PID2 register 240, 0=coasting, 1=cooling1, 2=cooling2, 3=cooling3, 4=heating1, 5=heating2, 6=heating3, 14=cooling4, 15=cooling5, 16=cooling6, 17=heating4, 18=heating5, 19=heating6.
395 | 1 | MODBUS_KEYPAD_SELECT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
396 | 1 | MODBUS_SPECIAL_MENU_LOCK | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
397 | 1 | MODBUS_DISPLAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | spare
398 | 1 | MODBUS_ICON | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ICON TABLE Set when certain icons are on/off ICON1 : TBD list the icons here, one for Tstat6 and one for Ttsat7 (TBD)day icon night icon heating icon cooling icon fan icon
399 | 1 | MODBUS_LAST_KEY_TIMER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Last key pressed counter. Minutes since the used last pressed a key.
400 | 1 | MODBUS_KEYPAD_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Keypad encoded value. Last keypress, READ ONLY
406 | 1 | MODBUS_MIN_ADDRESS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The minimum address which the device can accept, use this to limit addresses to a certain defined band.
407 | 1 | MODBUS_MAX_ADDRESS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The maximum device address can be set. The device address should between min and max address, default is 254
408 | 1 | MODBUS_EEPROM_SIZE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Show the size of E2 chip. 0 = 24c02, 1 = 24c08/24c16.
409 | 1 | MODBUS_TIMER_SELECT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Assign the timer to be used for which feature. 0 = period timer, 1 = rotation timer,2 = interlock, 3 = PWM timer
410 | 7 | MODBUS_RTC_DATA | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | RTC: year,month,week,day,hours,minutes,seconds data
434 | 1 | MODBUS_LCD_TURN_OFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | LCD turn off, 0 = turn off, 1 = normal
435 | 8 | MODBUS_SHOW_CHAR | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | Show User type message.
443 | 4 | MODBUS_INTERNAL_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Internal sensor name
447 | 4 | MODBUS_AI1_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Input 1 user name.
451 | 4 | MODBUS_AI2_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Input 2 user name.
455 | 4 | MODBUS_AI3_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Input 3 user name.
459 | 4 | MODBUS_AI4_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Input 4 user name.
463 | 4 | MODBUS_AI5_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Input 5 user name.
467 | 4 | MODBUS_AI6_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Input 6 user name.
471 | 4 | MODBUS_AI7_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Input 7 user name.
475 | 4 | MODBUS_AI8_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Input 8 user name.
479 | 4 | MODBUS_OUTPUT1_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Output 1 user name.
483 | 4 | MODBUS_OUTPUT2_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Output 2 user name.
487 | 4 | MODBUS_OUTPUT3_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Output 3 user name.
491 | 4 | MODBUS_OUTPUT4_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Output 4 user name.
495 | 4 | MODBUS_OUTPUT5_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Output 5 user name.
499 | 4 | MODBUS_OUTPUT6_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Output 6 user name.
503 | 4 | MODBUS_OUTPUT7_CHAR | 03_16 Read Holding and Write Multiple | Character String HI_LO | Output 7 user name.
539 | 1 | MODBUS_LCD_SCREEN1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | LCD screen1, select which information will display on LCD, range0 to 12
540 | 1 | MODBUS_LCD_SCREEN2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | LCD screen2, select which information will display on LCD, range0 to 12
541 | 1 | MODBUS_DEMAND_RESPONSE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Demand response flag 0: disable 1:yes 2:no
542 | 1 | MODBUS_LOCK_REGISTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (reserved)All registers except fan speed and manual input are not writable.0 = lock,1 = no lock
543 | 1 | MODBUS_PIR_STAGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Enable/disable PIR correspond 1/0 respectively.
564 | 1 | MODBUS_LCD_ROTATE_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | lcd rotate enable, decide how many items will be shown on rotate mode,range0 to 21.Display item select:0:none 1:temperature 2:setpoint 3:AI1 4:AI2 5:AI3 6:AI4 7:AI5 8:AI6 9:AI7 10:AI8 11:MODE 12:USER INFO 13:CLOCK DATE 14:CLOCK TIME 15:CO2 16: HUMIDITY
565 | 1 | MODBUS_SCHEDULE_ON_OFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | schedule enable/disable control bit. 0 = disable 1 = enable, default: enable
566 | 25 | MODBUS_DISPLAY_ITEM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | when reg564>0, rotate display enable, user can set the order of display items by these registers
591 | 1 | MODBUS_OUTPUT_PWM_AUTO_COAST | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PWM output range in COAST mode. 0 = CLOSE, 1 = OPEN, 2 = 0-100%, 3 = 50-100%, 4 = 0-50%. MSb 4 bits correspond to output4 and LSB 4 bits correspond to output5
592 | 1 | MODBUS_OUTPUT_PWM_AUTO_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PWM output range in COAST mode. 0 = CLOSE, 1 = OPEN, 2 = 0-100%, 3 = 50-100%, 4 = 0-50%. MSb 4 bits correspond to output4 and LSB 4 bits correspond to output6
593 | 1 | MODBUS_OUTPUT_PWM_AUTO_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PWM output range in COAST mode. 0 = CLOSE, 1 = OPEN, 2 = 0-100%, 3 = 50-100%, 4 = 0-50%. MSb 4 bits correspond to output4 and LSB 4 bits correspond to output7
594 | 1 | MODBUS_OUTPUT_PWM_AUTO_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PWM output range in COAST mode. 0 = CLOSE, 1 = OPEN, 2 = 0-100%, 3 = 50-100%, 4 = 0-50%. MSb 4 bits correspond to output4 and LSB 4 bits correspond to output8
595 | 1 | MODBUS_OUTPUT_PWM_AUTO_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PWM output range in COAST mode. 0 = CLOSE, 1 = OPEN, 2 = 0-100%, 3 = 50-100%, 4 = 0-50%. MSb 4 bits correspond to output4 and LSB 4 bits correspond to output9
596 | 1 | MODBUS_OUTPUT_PWM_AUTO_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PWM output range in COAST mode. 0 = CLOSE, 1 = OPEN, 2 = 0-100%, 3 = 50-100%, 4 = 0-50%. MSb 4 bits correspond to output4 and LSB 4 bits correspond to output10
597 | 1 | MODBUS_OUTPUT_PWM_AUTO_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PWM output range in COAST mode. 0 = CLOSE, 1 = OPEN, 2 = 0-100%, 3 = 50-100%, 4 = 0-50%. MSb 4 bits correspond to output4 and LSB 4 bits correspond to output11
598 | 1 | MODBUS_PWM1_OUT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PWM1 OUTPUT PERCENTAGE
599 | 1 | MODBUS_PWM2_OUT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PWM2 OUTPUT PERCENTAGE
602 | 1 | MODBUS_EXT_SENSOR_TEMP_CAL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibration data of thermistor which on external humidity sensor
607 | 1 | MODBUS_HUM_HEATER_CONTROL_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | humidity sensor heater control 0=not heat, 1=heating.
608 | 1 | MODBUS_HUM_INPUT_MANUAL_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | humidity sensor manual input enable 0=disable 1=enable.
609 | 1 | MODBUS_HUM_INPUT_MANUAL_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | humidity sensor manual input value, range: 0 to 1000
610 | 1 | MODBUS_CO2_INPUT_MANUAL_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 sensor manual input enable 0=disable 1=enable.
611 | 1 | MODBUS_CO2_INPUT_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 sensor manual input value, range: 0 to 3000
612 | 1 | MODBUS_CO2_CALIBRATION_DATA | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 sensor calibration data
613 | 1 | MODBUS_UNIVERSAL_OFF_OUTPUT_BEGIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 OFF TABLE COASTING
614 | 1 | MODBUS_UNIVERSAL_OFF_OUTPUT_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 OFF TABLE COOLING1
615 | 1 | MODBUS_UNIVERSAL_OFF_OUTPUT_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 OFF TABLE COOLING2
616 | 1 | MODBUS_UNIVERSAL_OFF_OUTPUT_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 OFF TABLE COOLING3
617 | 1 | MODBUS_UNIVERSAL_OFF_OUTPUT_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 OFF TABLE HEATING1
618 | 1 | MODBUS_UNIVERSAL_OFF_OUTPUT_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 OFF TABLE HEATING2
619 | 1 | MODBUS_UNIVERSAL_OFF_OUTPUT_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 OFF TABLE HEATING3
620 | 1 | MODBUS_UNIVERSAL_OFF_VALVE_BEGIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE OFF TABLE COASTING
621 | 1 | MODBUS_UNIVERSAL_OFF_VALVE_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE OFF TABLE COOLING1
622 | 1 | MODBUS_UNIVERSAL_OFF_VALVE_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE OFF TABLE COOLING2
623 | 1 | MODBUS_UNIVERSAL_OFF_VALVE_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE OFF TABLE COOLING3
624 | 1 | MODBUS_UNIVERSAL_OFF_VALVE_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE OFF TABLE HEATING1
625 | 1 | MODBUS_UNIVERSAL_OFF_VALVE_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE OFF TABLE HEATING2
626 | 1 | MODBUS_UNIVERSAL_OFF_VALVE_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE OFF TABLE HEATING3
627 | 1 | MODBUS_LIGHT_SENSOR_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Filter of light sensor
628 | 1 | MODBUS_LIGHT_SENSOR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | value of light sensor
629 | 1 | MODBUS_PIR_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PIR sensor select 1=PIR sensor enable 0=PIR sensor disable
630 | 1 | MODBUS_PIR_REAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIR sensor real value
631 | 1 | MODBUS_PIR_VALUE_ZERO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PIR sensor zero offset
632 | 1 | MODBUS_UNIVERSAL_VALVE_BEGIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE TABLE COASTING
633 | 1 | MODBUS_UNIVERSAL_VALVE_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE TABLE COOLING1
634 | 1 | MODBUS_UNIVERSAL_VALVE_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE TABLE COOLING2
635 | 1 | MODBUS_UNIVERSAL_VALVE_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE TABLE COOLING3
636 | 1 | MODBUS_UNIVERSAL_VALVE_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE TABLE HEATING1
637 | 1 | MODBUS_UNIVERSAL_VALVE_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE TABLE HEATING2
638 | 1 | MODBUS_UNIVERSAL_VALVE_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PID2 VALVE TABLE HEATING3
639 | 1 | MODBUS_ID_WRITE_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ID write protect. 0:enable ID write 1: disable ID write
641 | 1 | MODBUS_PIR_TIMER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PIR TIMER.
642 | 1 | MODBUS_SUPPLY_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) supply setpoint
643 | 1 | MODBUS_MAX_SUPPLY_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) Maximum supply setpoint
644 | 1 | MODBUS_MIN_SUPPLY_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) Minimal supply setpoint
645 | 1 | MODBUS_MAX_AIRFLOW_COOLING | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) Maximum airflow for cooling
646 | 1 | MODBUS_MAX_AIRFLOW_HEATING | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) Maximum airflow for heating
647 | 1 | MODBUS_MIN_AIRFLOW | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) Minimal airflow
648 | 1 | MODBUS_AIRFLOW_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) airflow setpoint
649 | 1 | MODBUS_VAV_CONTROL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) VAV function control bit0:VAV function enable/disable 0:(default)disable 1:enable bit1:airflow sensor present 0:NO 1:YES bit2: engineering units setting 0:in aireflow unit 1:in %
650 | 1 | MODBUS_PID3_INPUT_SELECT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) spare
651 | 1 | MODBUS_PID3_VALVE_OPERATION_TABLE_BEGIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OPERATION_TABLE_BEGIN
652 | 1 | MODBUS_PID3_VALVE_OPER_TABLE_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OPER_TABLE_COOL1
653 | 1 | MODBUS_PID3_VALVE_OPER_TABLE_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OPER_TABLE_COOL2
654 | 1 | MODBUS_PID3_VALVE_OPER_TABLE_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OPER_TABLE_COOL3
655 | 1 | MODBUS_PID3_VALVE_OPER_TABLE_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OPER_TABLE_HEAT1
656 | 1 | MODBUS_PID3_VALVE_OPER_TABLE_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OPER_TABLE_HEAT2
657 | 1 | MODBUS_PID3_VALVE_OPER_TABLE_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OPER_TABLE_HEAT3
658 | 1 | MODBUS_PID3_COOLING_DB | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3 cooling deadband
659 | 1 | MODBUS_PID3_HEATING_DB | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3 heating deadband
660 | 1 | MODBUS_PID3_PTERM | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (VAV function) PID3 Pterm
661 | 1 | MODBUS_PID3_ITERM | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | (VAV function) PID3 Iterm
662 | 1 | MODBUS_PID3_HEAT_STAGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3 heat stage(max 6 stages)
663 | 1 | MODBUS_PID3_COOL_STAGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3 cool stage(max 6 stages)
664 | 1 | MODBUS_PID3_OUTPUT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3 output
665 | 1 | MODBUS_PID3_OUTPUT_BEGIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OUTPUT_BEGIN
666 | 1 | MODBUS_PID3_OUTPUT_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OUTPUT_COOL1
667 | 1 | MODBUS_PID3_OUTPUT_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OUTPUT_COOL2
668 | 1 | MODBUS_PID3_OUTPUT_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OUTPUT_COOL3
669 | 1 | MODBUS_PID3_OUTPUT_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OUTPUT_HEAT1
670 | 1 | MODBUS_PID3_OUTPUT_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OUTPUT_HEAT2
671 | 1 | MODBUS_PID3_OUTPUT_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OUTPUT_HEAT3
672 | 1 | MODBUS_PID3_VALVE_OFF_TABLE_BEGIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OFF_TABLE_BEGIN
673 | 1 | MODBUS_PID3_VALVE_OFF_TABLE_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OFF_TABLE_COOL1
674 | 1 | MODBUS_PID3_VALVE_OFF_TABLE_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OFF_TABLE_COOL2
675 | 1 | MODBUS_PID3_VALVE_OFF_TABLE_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OFF_TABLE_COOL3
676 | 1 | MODBUS_PID3_VALVE_OFF_TABLE_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OFF_TABLE_HEAT1
677 | 1 | MODBUS_PID3_VALVE_OFF_TABLE_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OFF_TABLE_HEAT2
678 | 1 | MODBUS_PID3_VALVE_OFF_TABLE_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_VALVE_OFF_TABLE_HEAT3
679 | 1 | MODBUS_PID3_OFF_OUTPUT_BEGIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OFF_OUTPUT_BEGIN
680 | 1 | MODBUS_PID3_OFF_OUTPUT_COOL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OFF_OUTPUT_COOL1
681 | 1 | MODBUS_PID3_OFF_OUTPUT_COOL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OFF_OUTPUT_COOL2
682 | 1 | MODBUS_PID3_OFF_OUTPUT_COOL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OFF_OUTPUT_COOL3
683 | 1 | MODBUS_PID3_OFF_OUTPUT_HEAT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OFF_OUTPUT_HEAT1
684 | 1 | MODBUS_PID3_OFF_OUTPUT_HEAT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OFF_OUTPUT_HEAT2
685 | 1 | MODBUS_PID3_OFF_OUTPUT_HEAT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | (VAV function) PID3_DIGITAL_OFF_OUTPUT_HEAT3
691 | 1 | MODBUS_HEAT_COOL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | HEAT/COOL mode user
693 | 1 | MODBUS_CLEAR_EEPROM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | write 1 to clear EEPROM
695 | 1 | MODBUS_INTERNAL_SENSOR_MANUAL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Internal thermister manual value
705 | 1 | MODBUS_PID3_DAY_SP | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | PID3_DAY_SP
706 | 1 | MODBUS_PID3_NIGHT_SP | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | PID3_NIGHT_SP
712 | 1 | MODBUS_PWM_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0: relay pwm disable 10-100 set pwm duty
714 | 1 | MODBUS_TSTAT_NAME_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | TSTAT_NAME_ENABLE,//default value = 0x56 indicate tstat name function is present
715 | 10 | MODBUS_TSTAT_NAME | 03_16 Read Holding and Write Multiple | Character String HI_LO | TSTAT_NAME
725 | 1 | MODBUS_SHOW_ID | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | SHOW_ID //this regisger will let user display current ID, the time will depending on the written value
726 | 1 | MODBUS_TRANSDUCER_RANGE_MIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | TRANSDUCER_RANGE_MIN, //When set analog output to transducer mode, use these two reg to set range: range_min = 10 means 0V accodrding to 10C
727 | 1 | MODBUS_TRANSDUCER_RANGE_MAX | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | TRANSDUCER_RANGE_MAX
728 | 1 | MODBUS_ICON_MANUAL_MODE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ICON_MANUAL_MODE, //manual icons enable/disable 0:auto icon 1: manual icon
729 | 1 | MODBUS_ICON_MANUAL_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ICON_MANUAL_VALUE,//when set icon to munual mode, set value here
730 | 1 | MODBUS_SOFTWARE_RESET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 1: software reset
731 | 1 | MODBUS_CO2_AUTO_CAL_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0: enable co2 back ground calibration 1:disable
735 | 1 | MODBUS_PIR_SENSETIVITY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | set threshold for pir sensor, default:30
737 | 20 | MODBUS_FAN_MODE_NAME | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | fan mode name
769 | 1 | MODBUS_HUM_CALIBRATION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibration data of humidity sensor
770 | 1 | MODBUS_TEM_OF_HUM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | temperture of hum sensor
771 | 1 | MODBUS_SLEEP_COOLING_DB | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | cooling deadband of sleep mode
772 | 1 | MODBUS_SLEEP_HEATING_DB | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | heating deadband of sleep mode
773 | 1 | MODBUS_SLEEP_SP | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | setpoint of sleep mode
774 | 1 | MODBUS_SLEEP_COOLING_SP | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | cooling setpoint of sleep mode
775 | 1 | MODBUS_SLEEP_HEATING_SP | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | heating setpoint of sleep mode
776 | 1 | MODBUS_MAX_WORK_SP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | max setpoint for work setpoint
777 | 1 | MODBUS_MIN_WORK_SP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | min setpoint for work setpoint
778 | 1 | MODBUS_MAX_SLEEP_SP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | max setpoint for sleep setpoint
779 | 1 | MODBUS_MIN_SLEEP_SP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | min setpoint for sleep setpoint
780 | 1 | MODBUS_MAX_HOLIDAY_SP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | max setpoint for holiday setpoint
781 | 1 | MODBUS_MIN_HOLIDAY_SP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | min setpoint for holiday setpoint
782 | 1 | MODBUS_INPUT_VOLTAGE_ADJ | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | adjustment for voltage input default : 100
783 | 9 | MODBUS_ICON_CONTROL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | ICONs control for inputs
792 | 1 | MODBUS_PWM_OFF_TABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PWM off table
799 | 1 | MODBUS_DTERM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | D term for PID loop1
800 | 1 | MODBUS_PID SAMPLE_TIME | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | pid sample time, default: 1 second
801 | 1 | MODBUS_ZIGBEE_ID | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Zigbee module ID if zigbee moduble is present
802 | 1 | MODBUS_DELTA_TEM1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | delta temperature #1
803 | 1 | MODBUS_DELTA_TEM2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | delta temperature #2
804 | 1 | MODBUS_DELTA_TEMPERATURE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | delta temperature
813 | 12 | SCHEDULE_MONDAY_EVENT | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | (schedule)Monday event1 to 6 time:hour,minute
825 | 12 | SCHEDULE_TUESDAY_EVENT | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | (schedule)Tuesday event1 to 6 time:hour,minute
837 | 12 | SCHEDULE_WENSDAY_EVENT | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | (schedule)Wensday event1 to 6 time:hour,minute
849 | 12 | SCHEDULE_THURSDAY_EVENT | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | (schedule)Thursday event1 to 6 time:hour,minute
861 | 12 | SCHEDULE_FRIDAY_EVENT | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | (schedule)Friday event1 to 6 time:hour,minute
873 | 12 | SCHEDULE_SATDAY_EVENT | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | (schedule)Saturday event1 to 6 time:hour,minute
885 | 12 | SCHEDULE_SUNDAY_EVENT | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | (schedule)Sunday event1 to 6 time:hour,minute
897 | 12 | SCHEDULE_HOLIDAY_EVENT | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | (schedule)Holiday event1 to 6 time:hour,minute
909 | 16 | SCHEDULE_EVENT_FLAG | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | events mode for schdule 909-924
925 | 47 | SCHEDULE_HOLIDAY_DATA | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | holiday flag for the whole year 925-971
972 | 1 | MODBUS_AWAY_SP, | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | setpoint for away mode
973 | 1 | MODBUS_AWAY_COOLING_SP, | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | cooling setpoint for away mode
974 | 1 | MODBUS_AWAY_HEATING_SP, | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | heating setpoint for away mode
975 | 1 | MODBUS_AWAY_COOL_DB, | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | coolin deadband for away mode
976 | 1 | MODBUS_AWAY_HEAT_DB, | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | heatin deadband for away mode
977 | 1 | MODBUS_BACNET_STATION_NUM, | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | station number for bacnet protocol
979 | 1 | MODBUS_4TO20MA_BOTTOM, | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the lowest value for 4-20mA input table
980 | 1 | MODBUS_4TO20MA_TOP, | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the highest value for 4-20mA input table
981 | 1 | MODBUS_4TO20MA_UNIT_HI, | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | unit high bytes for 4-20mA input table
982 | 1 | MODBUS_4TO20MA_UNIT_LO, | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | unit low bytes for 4-20mA input table
991 | 1 | BACNET_INSTANCE_LOW, | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | instance low bytes for bacnet protocol
992 | 1 | BACNET_INSTANCE_HIGH, | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | instance high bytes for bacnet protocol
2000 | 1 | MODBUS_WIFI_ENABLE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 2 disable 1 enable other value means enable
2001 | 1 | MODBUS_WIFI_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI IP MODE , 0-DHCP,1-STATIC
2004 | 1 | MODBUS_WIFI_MODBUS_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WIFI_MODBUS_PORT ,Default value :502
2005 | 1 | MODBUS_WIFI_BACNET_PORT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | BACnet PORT , Default value :47808
2010 | 32 | MODBUS_WIFI_SSID | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | WIFI_SSID
2042 | 16 | MODBUS_WIFI_PASSWORD | 03_16 Read Holding and Write Multiple | 16 Bit Unsigned Integer | WIFI_PASSWORD
2058 | 12 | MODBUS_WIFI_IP_ADDRESS | 03_16 Read Holding and Write Multiple | 8 Bit Unsigned Integer | IP_ADDRESS
2070 | 1 | MODBUS_WIFI_MAC_ADDRESS_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2071 | 1 | MODBUS_WIFI_MAC_ADDRESS_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2072 | 1 | MODBUS_WIFI_MAC_ADDRESS_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2073 | 1 | MODBUS_WIFI_MAC_ADDRESS_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2074 | 1 | MODBUS_WIFI_MAC_ADDRESS_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2075 | 1 | MODBUS_WIFI_MAC_ADDRESS_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS

## PM5E_ARM
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | Serial Number - 4 byte value. Read-only
4 | 2 | MODBUS_VERSION_NUMBER_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Software Version – 2 byte value. Read-only
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | ADDRESS. Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Product Model. This is a read-only register that is used by the microcontroller to determine the product
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | [INVALID_DATA]
9 | 1 | MODBUS_PIC_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIC firmware version
10 | 1 | MODBUS_HUM_PIC_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIC version of Humidity module
11 | 1 | PLUG_N_PLAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Temporary address for plug-n-play addressing scheme
12 | 1 | ISP_MODE_INDICATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
14 | 1 | BASE_ADDRESS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | base address select
16 | 1 | MODBUS_UPDATE_STATUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Firmware Update Register, used to show the status of firmware updates.Writing 143 sets the config back to out of the box except for Modbus ID and baud rate. Write 159 to fix the current config as the user defaults, this is done automatically by T3000 any
17 | 1 | UPDATE_PTR_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | pointer for last attempt upload HI
18 | 1 | UPDATE_PTR_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | pointer for last attempt upload LO
19 | 1 | SCRATCHPAD_ADDRESS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Internal scratch pad address
20 | 2 | HARDWARE_INFORMATION | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | indicate if clock is present
21 | 1 | MODBUS_BACNET_SWITCH | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
51 | 1 | MODBUS_ZIGBEE_INDEX | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
52 | 1 | MODBUS_ZIGBEE_INFO1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
53 | 1 | MODBUS_ZIGBEE_INFO2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
54 | 1 | MODBUS_ZIGBEE_INFO3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
55 | 1 | MODBUS_ZIGBEE_INFO4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
56 | 1 | MODBUS_ZIGBEE_INFO5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
57 | 1 | MODBUS_ZIGBEE_INFO6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
58 | 1 | MODBUS_ZIGBEE_INFO7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
59 | 1 | MODBUS_ZIGBEE_INFO8 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
60 | 1 | MODBUS_ZIGBEE_INFO9 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
61 | 1 | MODBUS_ZIGBEE_INFO10 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
62 | 1 | MODBUS_ZIGBEE_INFO11 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
63 | 1 | MODBUS_ZIGBEE_INFO12 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
64 | 1 | MODBUS_ZIGBEE_INFO13 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
65 | 1 | MODBUS_ZIGBEE_INFO14 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
66 | 1 | MODBUS_ZIGBEE_INFO15 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
67 | 1 | MODBUS_ZIGBEE_INFO16 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
68 | 1 | MODBUS_ZIGBEE_INFO17 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
69 | 1 | MODBUS_ZIGBEE_INFO18 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
70 | 1 | MODBUS_ZIGBEE_INFO19 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
71 | 1 | MODBUS_ZIGBEE_INFO20 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
72 | 1 | MODBUS_ZIGBEE_INFO21 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
73 | 1 | MODBUS_ZIGBEE_INFO22 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
74 | 1 | MODBUS_ZIGBEE_INFO23 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
75 | 1 | MODBUS_ZIGBEE_INFO24 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
76 | 1 | MODBUS_ZIGBEE_INFO25 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
77 | 1 | MODBUS_ZIGBEE_INFO26 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
78 | 1 | MODBUS_ZIGBEE_INFO27 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
79 | 1 | MODBUS_ZIGBEE_INFO28 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
80 | 1 | MODBUS_ZIGBEE_INFO29 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
81 | 1 | MODBUS_ZIGBEE_INFO30 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
82 | 1 | MODBUS_ZIGBEE_INFO31 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
83 | 1 | MODBUS_ZIGBEE_INFO32 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
84 | 1 | MODBUS_ZIGBEE_INFO33 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
85 | 1 | MODBUS_ZIGBEE_INFO34 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
86 | 1 | MODBUS_ZIGBEE_INFO35 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
87 | 1 | MODBUS_ZIGBEE_INFO36 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
88 | 1 | MODBUS_ZIGBEE_INFO37 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
89 | 1 | MODBUS_ZIGBEE_INFO38 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
90 | 1 | MODBUS_ZIGBEE_INFO39 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
91 | 1 | MODBUS_ZIGBEE_INFO40 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
92 | 1 | MODBUS_ZIGBEE_INFO41 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
93 | 1 | MODBUS_ZIGBEE_INFO42 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
94 | 1 | MODBUS_ZIGBEE_INFO43 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
95 | 1 | MODBUS_ZIGBEE_INFO44 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
96 | 1 | MODBUS_ZIGBEE_INFO45 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
97 | 1 | MODBUS_ZIGBEE_INFO46 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
98 | 1 | MODBUS_ZIGBEE_INFO47 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
99 | 1 | MODBUS_ZIGBEE_INFO48 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
101 | 1 | TEMPRATURE_CHIP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Heating or cooling mode in effect
102 | 1 | TSTAT_COOLING_VALVE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Cooling valve position 0-1000 = 0-10V
103 | 1 | TSTAT_HEATING_VALVE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Heating valve position 0-1000 = 0-10V
104 | 1 | COOLING_PID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Cooling PI Term
105 | 1 | MODBUS_HEATING_PID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Heating PI Term
107 | 1 | PID1_MODE_OPERATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Current state of Tstat. High heat -> coasting -> high cool.
108 | 1 | TSTAT_DIGITAL_OUTPUT_STATUS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Relays 1,2,3 and, if on-off type, 4 and 5
109 | 1 | CALIBRATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
110 | 1 | MODBUS_CALIBRATION_ANALOG_IN1_SPAER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
111 | 1 | TEMP_SELECT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1= external sensor analog input 1 , 2 = internal thermistor, 3 = average the internal thermistor and analog input1
112 | 1 | TSTAT_DAC_OFFSET | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
113 | 1 | MODBUS_DELAY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
114 | 1 | COOLING_PTERM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
115 | 1 | COOLING_ITERM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
116 | 1 | MODBUS_HEATING_PTERM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
117 | 1 | MODBUS_HEATING_ITERM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0 50 Heating I term (1 %deg/min) - NOT USED IN REV25
118 | 1 | SEQUENCE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
119 | 1 | DAY_COOLING_DEADBAND | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1
120 | 1 | DAY_HEATING_DEADBAND | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1
121 | 1 | DEGC_OR_F | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
122 | 1 | FAN_MODE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
123 | 1 | NIGHT_HEATING_DEADBAND | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
124 | 1 | NIGHT_COOLING_DEADBAND | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
125 | 1 | APPLICATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
126 | 1 | POWERUP_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 15
127 | 1 | POWERUP_MODE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
128 | 1 | KEYPAD_SELECT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
129 | 1 | AUTO_ONLY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
130 | 1 | MODBUS_OUTPUT_SCALE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
131 | 1 | MAX_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 10
132 | 1 | MIN_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 10
133 | 1 | SPECIAL_MENU_LOCK | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
134 | 1 | FACTORY_DEFAULTS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
135 | 1 | DAY_COOLING_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 15
136 | 1 | DAY_HEATING_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 10
137 | 1 | FAN_SPEED | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
138 | 1 | FAN0_OPER_TABLE_COAST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1 byte, first 5 lsb shows the relay states, last 3 msb are spares
139 | 1 | FAN0_OPER_TABLE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1st byte is always coasting
140 | 1 | FAN0_OPER_TABLE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
141 | 1 | FAN0_OPER_TABLE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
142 | 1 | FAN0_OPER_TABLE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
143 | 1 | FAN0_OPER_TABLE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
144 | 1 | FAN0_OPER_TABLE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
145 | 1 | FAN1_OPER_TABLE_COAST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
146 | 1 | FAN1_OPER_TABLE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
147 | 1 | FAN1_OPER_TABLE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
148 | 1 | FAN1_OPER_TABLE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
149 | 1 | FAN1_OPER_TABLE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
150 | 1 | FAN1_OPER_TABLE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
151 | 1 | FAN1_OPER_TABLE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
152 | 1 | FAN2_OPER_TABLE_COAST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
153 | 1 | FAN2_OPER_TABLE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
154 | 1 | FAN2_OPER_TABLE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
155 | 1 | FAN2_OPER_TABLE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
156 | 1 | FAN2_OPER_TABLE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
157 | 1 | FAN2_OPER_TABLE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
158 | 1 | FAN2_OPER_TABLE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
159 | 1 | FAN3_OPER_TABLE_COAST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
160 | 1 | FAN3_OPER_TABLE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
161 | 1 | FAN3_OPER_TABLE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
162 | 1 | FAN3_OPER_TABLE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
163 | 1 | FAN3_OPER_TABLE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
164 | 1 | FAN3_OPER_TABLE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
165 | 1 | FAN3_OPER_TABLE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
166 | 1 | FANAUT_OPER_TABLE_COAST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
167 | 1 | FANAUT_OPER_TABLE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
168 | 1 | FANAUT_OPER_TABLE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
169 | 1 | FANAUT_OPER_TABLE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
170 | 1 | FANAUT_OPER_TABLE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
171 | 1 | FANAUT_OPER_TABLE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
172 | 1 | FANAUT_OPER_TABLE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
173 | 1 | VALVE_OPER_TABLE_BEGIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
174 | 1 | VALVE_OPER_TABLE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
175 | 1 | VALVE_OPER_TABLE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
176 | 1 | VALVE_OPER_TABLE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
177 | 1 | VALVE_OPER_TABLE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
178 | 1 | VALVE_OPER_TABLE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
179 | 1 | VALVE_OPER_TABLE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
180 | 1 | MODBUS_EXTERNAL_SENSOR_0 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | External Sensor 0 reading
181 | 1 | MODBUS_EXTERNAL_SENSOR_1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | External Sensor 1 reading
182 | 1 | NIGHT_HEATING_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
183 | 1 | NIGHT_COOLING_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
184 | 1 | INFO_BYTE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
185 | 1 | BAUDRATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
186 | 1 | OUTPUT1_SCALE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
187 | 1 | OUTPUT2_SCALE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
188 | 1 | MODBUS_ANALOG_IN1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
189 | 1 | MODBUS_ANALOG_IN2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
190 | 1 | MODBUS_DIGITAL_IN1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
191 | 1 | OUTPUT1_DELAY_OFF_TO_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
192 | 1 | OUTPUT2_DELAY_OFF_TO_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
193 | 1 | OUTPUT3_DELAY_OFF_TO_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
194 | 1 | OUTPUT4_DELAY_OFF_TO_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
195 | 1 | OUTPUT5_DELAY_OFF_TO_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
196 | 1 | OUTPUT1_DELAY_ON_TO_OFF | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
197 | 1 | OUTPUT2_DELAY_ON_TO_OFF | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
198 | 1 | OUTPUT3_DELAY_ON_TO_OFF | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
199 | 1 | OUTPUT4_DELAY_ON_TO_OFF | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
200 | 1 | OUTPUT5_DELAY_ON_TO_OFF | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
201 | 1 | CYCLING_DELAY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
202 | 1 | CHANGOVER_DELAY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
203 | 1 | MODBUS_DISPLAY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
204 | 1 | MODBUS_LED1_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
205 | 1 | MODBUS_LED2_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
206 | 1 | MODBUS_LED3_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
207 | 1 | MODBUS_LED4_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0 22 Determines what controls the state of the LED
208 | 1 | MODBUS_LED5_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
209 | 1 | MODBUS_LED6_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
210 | 1 | MODBUS_LED7_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
211 | 1 | TSTAT_OVERRIDE_TIMER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0
212 | 1 | OVERRIDE_TIMER_LEFT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
213 | 1 | FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0 = OFF, 1 = trigger unoccupied on falling edge, 2 = occupied high, unoccupied low
214 | 1 | HEAT_COOL_CONFIG | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
215 | 1 | MODBUS_INTERNAL_TEMP_IC | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
216 | 1 | INTERNAL_THERMISTOR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
217 | 1 | CALIBRATION_INTERNAL_THERMISTOR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
218 | 1 | MODBUS_CALIBRATION_ANALOG_IN2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
219 | 1 | TABLE1_ZERO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1 254 the range from reg 20 to reg 41.A changable look up table for "custom" sensor
220 | 1 | TABLE1_HALFONE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
221 | 1 | TABLE1_ONE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
222 | 1 | TABLE1_HALFTWO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
223 | 1 | TABLE1_TWO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
224 | 1 | TABLE1_HALFTHREE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
225 | 1 | TABLE1_THREE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
226 | 1 | TABLE1_HALFFOUR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
227 | 1 | TABLE1_FOUR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
228 | 1 | TABLE1_HALFFIVE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
229 | 1 | TABLE1_FIVE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
230 | 1 | TABLE2_ZERO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
231 | 1 | TABLE2_HALFONE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
232 | 1 | TABLE2_ONE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
233 | 1 | TABLE2_HALFTWO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
234 | 1 | TABLE2_TWO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
235 | 1 | TABLE2_HALFTHREE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
236 | 1 | TABLE2_THREE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
237 | 1 | TABLE2_HALFFOUR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
238 | 1 | TABLE2_FOUR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
239 | 1 | TABLE2_HALFFIVE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
240 | 1 | TABLE2_FIVE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
241 | 1 | INPUT1_SELECT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1 254 reg 241 select which way the analog input is
242 | 1 | UNIVERSAL_HEAT_DB | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | universal heating deadband
243 | 1 | UNIVERSAL_COOL_DB | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | universal heating deadband
244 | 1 | UNIVERSAL_PTERM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1 254 reg 244 is the address of P term a universal PID
245 | 1 | UNIVERSAL_ITERM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1 254 reg 245 is the address of I term a universal PID
246 | 1 | UNIVERSAL_SET | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | reg 246 is the setpoint for universal PID
247 | 1 | PID_OUTPUT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | reg 247 select which type PID to be caculate for control output
248 | 1 | PID_OUTPUT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
249 | 1 | PID_OUTPUT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
250 | 1 | PID_OUTPUT4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
251 | 1 | PID_OUTPUT5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
252 | 1 | PID_OUTPUT6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
253 | 1 | PID_OUTPUT7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
254 | 1 | UNIVERSAL_OUTPUT_BEGIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | control OUTPUT_1TO5,there are 7 status
255 | 1 | UNIVERSAL_OUTPUT_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
256 | 1 | UNIVERSAL_OUTPUT_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
257 | 1 | UNIVERSAL_OUTPUT_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
258 | 1 | UNIVERSAL_OUTPUT_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
259 | 1 | UNIVERSAL_OUTPUT_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
260 | 1 | UNIVERSAL_OUTPUT_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
261 | 1 | UNIVERSAL_VALVE_BEGIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | control the status of valve
262 | 1 | UNIVERSAL_VALVE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
263 | 1 | UNIVERSAL_VALVE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
264 | 1 | UNIVERSAL_VALVE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
265 | 1 | UNIVERSAL_VALVE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
266 | 1 | UNIVERSAL_VALVE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
267 | 1 | UNIVERSAL_VALVE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
268 | 1 | HEAT_UNIVERSAL_TABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
269 | 1 | COOL_UNIVERSAL_TABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
270 | 1 | TSTAT_PID_UNIVERSAL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
271 | 1 | UNITS1_HIGH | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
272 | 1 | UNITS1_LOW | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
273 | 1 | UNITS2_HIGH | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
274 | 1 | UNITS2_LOW | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
275 | 1 | UNIVERSAL_NIGHTSET | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
276 | 1 | HEAT_ORIGINAL_TABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
277 | 1 | COOL_ORIGINAL_TABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
278 | 1 | TSTAT_PID2_MODE_OPERATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
279 | 1 | VALVE_TRAVEL_TIME | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
280 | 1 | MODE_OUTPUT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 202
281 | 1 | MODE_OUTPUT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
282 | 1 | MODE_OUTPUT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
283 | 1 | MODE_OUTPUT4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
284 | 1 | MODE_OUTPUT5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
285 | 1 | VALVE_PERCENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
286 | 1 | INTERLOCK_OUTPUT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
287 | 1 | INTERLOCK_OUTPUT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
288 | 1 | INTERLOCK_OUTPUT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
289 | 1 | INTERLOCK_OUTPUT4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
290 | 1 | INTERLOCK_OUTPUT5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
291 | 1 | INTERLOCK_OUTPUT6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
292 | 1 | INTERLOCK_OUTPUT7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
293 | 1 | SETPOINT_INCREASE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
294 | 1 | LAST_KEY_TIMER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
295 | 1 | FREEZE_TEMP_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
296 | 1 | FREEZE_DELAY_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
297 | 1 | FREEZE_DELAY_OFF | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
298 | 1 | ANALOG1_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
299 | 1 | ANALOG2_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
300 | 1 | MODBUS_DIGITAL1_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
301 | 1 | TIMER_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
302 | 1 | TIMER_OFF | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
303 | 1 | TIMER_UNITS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
304 | 1 | TSTAT_KEYPAD_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
305 | 1 | DISPLAY_HUNDRED | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
306 | 1 | DISPLAY_TEN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
307 | 1 | DISPLAY_DIGITAL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
308 | 1 | DISPLAY_STATUS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
309 | 1 | INPUT_MANU_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
310 | 1 | OUTPUT_MANU_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
311 | 1 | MODBUS_DIGITAL_INPUT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
312 | 1 | DEADMASTER_AUTO_MANUAL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | DEADMASTER_AUTO_MANUAL = 1, the output will be trigger to "AUTO" mode //DEADMASTER_AUTO_MANUAL = 0, the default, outputs will not change, stay in whatever mode they were last commanded
313 | 1 | DEADMASTER_OUTPUT_STATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | (relay1-5) deadmaster config value during deadmaster be triggered
314 | 1 | DEADMASTER_COOL_OUTPUT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | (analog output - cooling)deadmaster config value during deadmaster be triggered
315 | 1 | DEADMASTER_HEAT_OUTPUT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
316 | 1 | MODBUS_DEBUGTIMER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
317 | 1 | DEAD_MASTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
318 | 1 | ROUND_DISPLAY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
319 | 1 | MIN_ADDRESS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | The ID of tstat should be in the range MIN and MAX address
320 | 1 | MAX_ADDRESS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
321 | 1 | MODBUS_FAN_GRIDPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
322 | 1 | MODBUS_MODE_GRIDPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
323 | 1 | MODBUS_HOLD_GRIDPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
324 | 1 | MODBUS_CONFIGURATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
325 | 1 | MODBUS_UTIL_MODE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
326 | 1 | EEPROM_SIZE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
327 | 1 | TIMER_SELECT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
328 | 1 | OUTPUT1_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
329 | 1 | MODBUS_ROTATION_OUT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
330 | 1 | MODBUS_ROTATION_OUT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
331 | 1 | MODBUS_ROTATION_OUT4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
332 | 1 | MODBUS_ROTATION_OUT5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
333 | 1 | MODBUS_ROTATION_TIME_LEFT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
334 | 1 | OUTPUT2_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
335 | 1 | OUTPUT3_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
336 | 1 | OUTPUT4_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
337 | 1 | OUTPUT5_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
338 | 1 | DEFAULT_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
339 | 1 | SETPOINT_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
340 | 1 | PIR_STAGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
341 | 1 | OUTPUT_PWM_AUTO_COAST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
342 | 1 | OUTPUT_PWM_AUTO_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
343 | 1 | OUTPUT_PWM_AUTO_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
344 | 1 | OUTPUT_PWM_AUTO_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
345 | 1 | OUTPUT_PWM_AUTO_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
346 | 1 | OUTPUT_PWM_AUTO_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
347 | 1 | OUTPUT_PWM_AUTO_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
348 | 1 | PWM_OUT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
349 | 1 | PWM_OUT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
350 | 1 | FREE_COOL_CONFIG | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Free cool configure register.bit0,free cool enable/disable,0 = disable,1= enable.
351 | 1 | VALVE_OFF_TABLE_COAST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | OFF table for analog output,
352 | 1 | VALVE_OFF_TABLE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
353 | 1 | VALVE_OFF_TABLE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
354 | 1 | VALVE_OFF_TABLE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
355 | 1 | VALVE_OFF_TABLE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
356 | 1 | VALVE_OFF_TABLE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
357 | 1 | VALVE_OFF_TABLE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
358 | 1 | LOCK_REGISTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
359 | 1 | ANALOG1_RANGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
360 | 1 | ANALOG2_RANGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
361 | 1 | ANALOG3_RANGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
362 | 1 | ANALOG4_RANGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
363 | 1 | ANALOG5_RANGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
364 | 1 | ANALOG6_RANGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
365 | 1 | ANALOG7_RANGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
366 | 1 | ANALOG8_RANGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
367 | 1 | ANALOG_INPUT1_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
368 | 1 | ANALOG_INPUT2_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
369 | 1 | ANALOG_INPUT3_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
370 | 1 | ANALOG_INPUT4_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
371 | 1 | ANALOG_INPUT5_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
372 | 1 | ANALOG_INPUT6_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
373 | 1 | ANALOG_INPUT7_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
374 | 1 | ANALOG_INPUT8_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
375 | 1 | CALIBRATION_ANALOG1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
376 | 1 | CALIBRATION_ANALOG2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
377 | 1 | CALIBRATION_ANALOG3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
378 | 1 | CALIBRATION_ANALOG4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
379 | 1 | CALIBRATION_ANALOG5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
380 | 1 | CALIBRATION_ANALOG6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
381 | 1 | CALIBRATION_ANALOG7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
382 | 1 | CALIBRATION_ANALOG8 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
383 | 1 | MODBUS_LINE1_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
384 | 1 | MODBUS_LINE1_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
385 | 1 | MODBUS_LINE1_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
386 | 1 | MODBUS_LINE1_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
387 | 1 | MODBUS_LINE1_CHAR5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
388 | 1 | MODBUS_LINE1_CHAR6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
389 | 1 | MODBUS_LINE1_CHAR7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
390 | 1 | MODBUS_LINE1_CHAR8 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
391 | 1 | MODBUS_LINE2_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
392 | 1 | MODBUS_LINE2_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
393 | 1 | MODBUS_LINE2_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
394 | 1 | MODBUS_LINE2_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
395 | 1 | MODBUS_LINE2_CHAR5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
396 | 1 | MODBUS_LINE2_CHAR6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
397 | 1 | MODBUS_LINE2_CHAR7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
398 | 1 | MODBUS_LINE2_CHAR8 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
399 | 1 | LCD_TURN_OFF | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
400 | 1 | LCD_SCREEN1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
401 | 1 | LCD_SCREEN2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
402 | 1 | SUN_ICON_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
403 | 1 | MOON_ICON_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
404 | 1 | TSTAT_HEAT_COOL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
405 | 1 | MODBUS_DELAY1_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
406 | 1 | MODBUS_DELAY2_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
407 | 1 | MODBUS_DELAY3_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
408 | 1 | MODBUS_DELAY4_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
409 | 1 | MODBUS_DELAY5_ON_TO_OFF_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
410 | 1 | MODBUS_DELAY1_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
411 | 1 | MODBUS_DELAY2_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
412 | 1 | MODBUS_DELAY3_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
413 | 1 | MODBUS_DELAY4_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
414 | 1 | MODBUS_DELAY5_OFF_TO_ON_TIME_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
415 | 1 | MODBUS_OAT_HOTTEST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 415 Outside air temperature in hottest day
416 | 1 | MODBUS_OAT_COLDEST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 416 Outside air temperature in coldest day
417 | 1 | MODBUS_OFFSET_HOTTEST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 417 Offset in hottest day
418 | 1 | MODBUS_OFFSET_COLDEST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
419 | 1 | MODBUS_CURRENT_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 419 Crrent setpoint = user setpoint + offset setpoint
420 | 1 | MODBUS_SETPOINT_OFFSET | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 420 Setpoint offset
421 | 1 | MODBUS_TURN_OFF_FAN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
422 | 1 | DAY_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
423 | 1 | DAYSETPOINT_OPTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
424 | 1 | MODBUS_WINDOW_INTERLOCK_DELAY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
425 | 1 | LINE1_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
426 | 1 | LINE1_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
427 | 1 | LINE1_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
428 | 1 | LINE1_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
429 | 1 | LINE2_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
430 | 1 | LINE2_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
431 | 1 | LINE2_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
432 | 1 | LINE2_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
433 | 1 | INTERNAL_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
434 | 1 | INTERNAL_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
435 | 1 | INTERNAL_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
436 | 1 | INTERNAL_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
437 | 1 | AI1_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | input1 user input description
438 | 1 | AI1_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
439 | 1 | AI1_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
440 | 1 | AI1_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
441 | 1 | AI2_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | input2 user input description
442 | 1 | AI2_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
443 | 1 | AI2_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
444 | 1 | AI2_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
445 | 1 | AI3_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | input3 user input description
446 | 1 | AI3_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
447 | 1 | AI3_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
448 | 1 | AI3_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
449 | 1 | AI4_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | input4 user input description
450 | 1 | AI4_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
451 | 1 | AI4_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
452 | 1 | AI4_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
453 | 1 | AI5_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | input5 user input description
454 | 1 | AI5_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
455 | 1 | AI5_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
456 | 1 | AI5_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
457 | 1 | AI6_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | input6 user input description
458 | 1 | AI6_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
459 | 1 | AI6_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
460 | 1 | AI6_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
461 | 1 | AI7_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | input7 user input description
462 | 1 | AI7_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
463 | 1 | AI7_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
464 | 1 | AI7_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
465 | 1 | AI8_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | input8 user input description
466 | 1 | AI8_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
467 | 1 | AI8_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
468 | 1 | AI8_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
469 | 1 | OUTPUT1_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output1 user output description
470 | 1 | OUTPUT1_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
471 | 1 | OUTPUT1_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
472 | 1 | OUTPUT1_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
473 | 1 | OUTPUT2_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output2 user output description
474 | 1 | OUTPUT2_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
475 | 1 | OUTPUT2_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
476 | 1 | OUTPUT2_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
477 | 1 | OUTPUT3_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output3 user output description
478 | 1 | OUTPUT3_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
479 | 1 | OUTPUT3_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
480 | 1 | OUTPUT3_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
481 | 1 | OUTPUT4_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output4 user output description
482 | 1 | OUTPUT4_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
483 | 1 | OUTPUT4_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
484 | 1 | OUTPUT4_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
485 | 1 | OUTPUT5_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output5 user output description
486 | 1 | OUTPUT5_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
487 | 1 | OUTPUT5_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
488 | 1 | OUTPUT5_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
489 | 1 | OUTPUT6_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output6 user output description
490 | 1 | OUTPUT6_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
491 | 1 | OUTPUT6_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
492 | 1 | OUTPUT6_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
493 | 1 | OUTPUT7_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | output7 user output description
494 | 1 | OUTPUT7_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
495 | 1 | OUTPUT7_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
496 | 1 | OUTPUT7_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
497 | 1 | LCD_ROTATE_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
498 | 1 | DISP_ITEM_TEMPERATURE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
499 | 1 | DISP_ITEM_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
500 | 1 | DISP_ITEM_AI1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
501 | 1 | DISP_ITEM_AI2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
502 | 1 | DISP_ITEM_AI3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
503 | 1 | DISP_ITEM_AI4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
504 | 1 | DISP_ITEM_AI5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
505 | 1 | DISP_ITEM_AI6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
506 | 1 | DISP_ITEM_AI7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
507 | 1 | DISP_ITEM_AI8 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
508 | 1 | DISP_ITEM_OUT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
509 | 1 | DISP_ITEM_OUT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
510 | 1 | DISP_ITEM_OUT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
511 | 1 | DISP_ITEM_OUT4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
512 | 1 | DISP_ITEM_OUT5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
513 | 1 | DISP_ITEM_OUT6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
514 | 1 | DISP_ITEM_OUT7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
515 | 1 | DISP_ITEM_MODE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
516 | 1 | DISP_ITEM_USER_INFO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
517 | 1 | DISP_ITEM_CLOCK_DATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
518 | 1 | DISP_ITEM_CLOCK_TIME | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
519 | 1 | RTC_YEAR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
520 | 1 | RTC_MONTH | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
521 | 1 | RTC_WEEK | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
522 | 1 | RTC_DAY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
523 | 1 | RTC_HOUR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
524 | 1 | RTC_MINUTE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
525 | 1 | RTC_SECOND | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
526 | 1 | UNIVERSAL_OFF_TABLE_BEGIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PID2 ON/OFF mode off tabale
527 | 1 | UNIVERSAL_OFF_TABLE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
528 | 1 | UNIVERSAL_OFF_TABLE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
529 | 1 | UNIVERSAL_OFF_TABLE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
530 | 1 | UNIVERSAL_OFF_TABLE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
531 | 1 | UNIVERSAL_OFF_TABLE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
532 | 1 | UNIVERSAL_OFF_TABLE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
533 | 1 | UNIVERSAL_OFF_VALVE_BEGIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PID2 valve mode off tabale
534 | 1 | UNIVERSAL_OFF_VALVE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
535 | 1 | UNIVERSAL_OFF_VALVE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
536 | 1 | UNIVERSAL_OFF_VALVE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
537 | 1 | UNIVERSAL_OFF_VALVE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
538 | 1 | UNIVERSAL_OFF_VALVE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
539 | 1 | UNIVERSAL_OFF_VALVE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
540 | 1 | MODBUS_WINDOW_HEATING_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
541 | 1 | MODBUS_WINDOW_COOLING_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
542 | 1 | MODBUS_RELAY_PWM_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
543 | 1 | MODBUS_RELAY_PWM_TOTAL_DUTY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
544 | 1 | MODBUS_RELAY_PWM_HIGH_DUTY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
545 | 1 | MODBUS_DIGITAL_INPUT_MANUAL_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
546 | 1 | MODBUS_DIGITAL_INPUT_RANGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
547 | 1 | INPUT1_FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
548 | 1 | INPUT2_FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
549 | 1 | INPUT3_FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
550 | 1 | INPUT4_FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
551 | 1 | INPUT5_FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
552 | 1 | INPUT6_FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
553 | 1 | INPUT7_FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
554 | 1 | INPUT8_FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
555 | 1 | MODBUS_OUTPUT_OFF_TABLE_CYCLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
556 | 1 | MODBUS_OUTPUT_HEAT_TABLE_CYCLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
557 | 1 | MODBUS_OUTPUT_COOL_TABLE_CYCLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
558 | 1 | MODBUS_OUTPUT_GAS_TABLE_CYCLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
559 | 1 | MODBUS_OUTPUT_AUTO_TABLE_CYCLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
560 | 1 | MODBUS_OUTPUT_CYCLE_OFF_TIME | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
561 | 1 | MODBUS_OUTPUT_CYCLE_ON_TIME | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
562 | 1 | MODBUS_OUTPUT_CYCLE_UNIT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0 = second 1 = minute, just use minute for now
563 | 1 | MODBUS_COOL_HYSTERISIS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
564 | 1 | MODBUS_HEAT_HYSTERISIS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
565 | 1 | MODBUS_SANJAY_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
566 | 1 | MODBUS_DEMIST_MODE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
567 | 1 | MODBUS_FAN_MANUAL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
568 | 1 | TSTAT_ID_WRITE_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
569 | 1 | SUPPLY_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
570 | 1 | MAX_SUPPLY_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
571 | 1 | MIN_SUPPLY_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
572 | 1 | MAX_AIRFLOW_COOLING | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
573 | 1 | MAX_AIRFLOW_HEATING | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
574 | 1 | OCC_MIN_AIRFLOW | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
575 | 1 | AIRFLOW_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
576 | 1 | VAV_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
577 | 1 | PID3_INPUT_SELECT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
578 | 1 | PID3_VALVE_OPER_TABLE_BEGIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
579 | 1 | PID3_VALVE_OPER_TABLE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
580 | 1 | PID3_VALVE_OPER_TABLE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
581 | 1 | PID3_VALVE_OPER_TABLE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
582 | 1 | PID3_VALVE_OPER_TABLE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
583 | 1 | PID3_VALVE_OPER_TABLE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
584 | 1 | PID3_VALVE_OPER_TABLE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
585 | 1 | PID3_COOLING_DB | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
586 | 1 | PID3_HEATING_DB | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
587 | 1 | PID3_PTERM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
588 | 1 | PID3_ITERM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
589 | 1 | PID3_HEAT_STAGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
590 | 1 | PID3_COOL_STAGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
591 | 1 | PID3_OUTPUT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
592 | 1 | PID3_OUTPUT_BEGIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | control OUTPUT_1TO5,there are 7 status
593 | 1 | PID3_OUTPUT_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
594 | 1 | PID3_OUTPUT_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
595 | 1 | PID3_OUTPUT_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
596 | 1 | PID3_OUTPUT_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
597 | 1 | PID3_OUTPUT_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
598 | 1 | PID3_OUTPUT_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
599 | 1 | OUTPUT6_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
600 | 1 | OUTPUT7_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
601 | 1 | ANALOG3_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
602 | 1 | ANALOG4_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
603 | 1 | ANALOG5_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
604 | 1 | ANALOG6_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
605 | 1 | ANALOG7_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
606 | 1 | PID3_VALVE_OFF_TABLE_BEGIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
607 | 1 | PID3_VALVE_OFF_TABLE_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
608 | 1 | PID3_VALVE_OFF_TABLE_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
609 | 1 | PID3_VALVE_OFF_TABLE_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
610 | 1 | PID3_VALVE_OFF_TABLE_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
611 | 1 | PID3_VALVE_OFF_TABLE_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
612 | 1 | PID3_VALVE_OFF_TABLE_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
613 | 1 | PID3_OFF_OUTPUT_BEGIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
614 | 1 | PID3_OFF_OUTPUT_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
615 | 1 | PID3_OFF_OUTPUT_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
616 | 1 | PID3_OFF_OUTPUT_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
617 | 1 | PID3_OFF_OUTPUT_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
618 | 1 | PID3_OFF_OUTPUT_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
619 | 1 | PID3_OFF_OUTPUT_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
620 | 1 | SHOW_ID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | this regisger will let user display current ID, the time will depending on the written value
621 | 1 | NIGHT_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
622 | 1 | MANUAL_AO1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
623 | 1 | MANUAL_AO2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
624 | 1 | PID3_DAY_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
625 | 1 | PID3_NIGHT_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
626 | 1 | TSTAT_NAME_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | default value = 0x55 indicate tstat name function is present
627 | 1 | TSTAT_NAME1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
628 | 1 | TSTAT_NAME2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
629 | 1 | TSTAT_NAME3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
630 | 1 | TSTAT_NAME4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
631 | 1 | TSTAT_NAME5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
632 | 1 | TSTAT_NAME6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
633 | 1 | TSTAT_NAME7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
634 | 1 | TSTAT_NAME8 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
635 | 1 | TSTAT_NAME9 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
636 | 1 | TSTAT_NAME10 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
637 | 1 | OUTPUT_PWM_OFF_COAST | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | out4 and out5 pwm table
638 | 1 | OUTPUT_PWM_OFF_COOL1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
639 | 1 | OUTPUT_PWM_OFF_COOL2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
640 | 1 | OUTPUT_PWM_OFF_COOL3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
641 | 1 | OUTPUT_PWM_OFF_HEAT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
642 | 1 | OUTPUT_PWM_OFF_HEAT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
643 | 1 | OUTPUT_PWM_OFF_HEAT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
644 | 1 | DTERM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
645 | 1 | PID_SAMPLE_TIME | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
646 | 1 | SCHEDULE_ON_OFF | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1:ON 0:OFF//END OF PM5E REGISTERS
647 | 1 | SYSTEM_TIME_FORMAT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | system format
648 | 1 | RS485_MODE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
649 | 1 | EXTERNAL_SENSOR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CO2
650 | 1 | EXTERNAL_SENSOR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | HUM
651 | 1 | CO2_FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
652 | 1 | HUM_FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
653 | 1 | TSTAT_HUMCOUNT1_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | sensor frequency
654 | 1 | TSTAT_HUMRH1_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | calibration point
655 | 1 | TSTAT_HUMCOUNT2_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
656 | 1 | TSTAT_HUMRH2_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
657 | 1 | ANALOG8_FUNCTION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
658 | 1 | TSTAT_HUMIDITY_RH | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | relative humidity in percentage
659 | 1 | TSTAT_HUMIDITY_FREQUENCY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw frequency reading
660 | 1 | TSTAT_HUM_PIC_UPDATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | write current calibration table to PIC, which table decided by register 427
661 | 1 | TSTAT_HUM_CAL_NUM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | calibration data number
662 | 1 | TSTAT_HUM_CURRENT_DEFAULT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | decide which table will run, default tabel or customer table current=1 default=0
663 | 1 | MANU_RELAY1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
664 | 1 | MANU_RELAY2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
665 | 1 | MANU_RELAY3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
666 | 1 | MANU_RELAY4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
667 | 1 | MANU_RELAY5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
668 | 1 | MIDDLE_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
669 | 1 | WINDOW_INTERLOCK_COOLING_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
670 | 1 | WINDOW_INTERLOCK_HEATING_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
671 | 1 | ECOMONY_COOLING_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
672 | 1 | ECOMONY_HEATING_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
673 | 1 | MAX_SETPOINT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
674 | 1 | MIN_SETPOINT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
675 | 1 | MAX_SETPOINT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
676 | 1 | MIN_SETPOINT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
677 | 1 | MAX_SETPOINT4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
678 | 1 | MIN_SETPOINT4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
679 | 1 | WALL_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | wall setpoint ,normal setpoint
680 | 1 | CEILING_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | celling setpoint
681 | 1 | AVERAGE_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
682 | 1 | UNOCCUPIED_HEATING | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
683 | 1 | UNOCCUPIED_COOLING | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
684 | 1 | RH_SETPOINT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
685 | 1 | DISPLAY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Display setting. 0 = temperature, 1 = setpoint
686 | 1 | ICON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
687 | 1 | DIAGNOSTIC_ALARM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
688 | 1 | SCHEDULE_DHOME_HOUR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
689 | 1 | SCHEDULE_DHOME_MIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
690 | 1 | SCHEDULE_WORK_HOUR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
691 | 1 | SCHEDULE_WORK_MIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
692 | 1 | SCHEDULE_NHOME_HOUR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
693 | 1 | SCHEDULE_NHOME_MIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
694 | 1 | SCHEDULE_SLEEP_HOUR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
695 | 1 | SCHEDULE_SLEEP_MIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
696 | 1 | SCHEDULE_HOLIDAY_BYEAR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
697 | 1 | SCHEDULE_HOLIDAY_BMONTH | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
698 | 1 | SCHEDULE_HOLIDAY_BDAY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
699 | 1 | SCHEDULE_HOLIDAY_EYEAR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
700 | 1 | SCHEDULE_HOLIDAY_EMONTH | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
701 | 1 | SCHEDULE_HOLIDAY_EDAY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
702 | 1 | DAY2_EVENT4_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
703 | 1 | DAY2_EVENT4_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
704 | 1 | SCHEDULEA_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
705 | 1 | SCHEDULEA_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
706 | 1 | SCHEDULEA_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
707 | 1 | SCHEDULEA_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
708 | 1 | SCHEDULEB_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
709 | 1 | SCHEDULEB_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
710 | 1 | SCHEDULEB_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
711 | 1 | SCHEDULEB_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
712 | 1 | SCHEDULEC_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
713 | 1 | SCHEDULEC_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
714 | 1 | SCHEDULEC_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
715 | 1 | SCHEDULEC_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
716 | 1 | SCHEDULED_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
717 | 1 | SCHEDULED_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
718 | 1 | SCHEDULED_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
719 | 1 | SCHEDULED_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
720 | 1 | WALL_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
721 | 1 | WALL_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
722 | 1 | WALL_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
723 | 1 | WALL_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
724 | 1 | CEILING_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
725 | 1 | CEILING_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
726 | 1 | CEILING_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
727 | 1 | CEILING_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
728 | 1 | OUTDOOR_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
729 | 1 | OUTDOOR_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
730 | 1 | OUTDOOR_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
731 | 1 | OUTDOOR_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
732 | 1 | AVERAGE_CHAR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
733 | 1 | AVERAGE_CHAR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
734 | 1 | AVERAGE_CHAR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
735 | 1 | AVERAGE_CHAR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
736 | 1 | DEMAND_RESPONSE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
737 | 1 | FIRST_CAL_FLAG | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | picdataok
738 | 1 | BAC_INSTANCE_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | erease current PIC calibration data table
739 | 1 | BAC_INSTANCE_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
740 | 1 | RTC_HUMRH3_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
741 | 1 | RTC_HUMCOUNT4_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
742 | 1 | RTC_HUMRH4_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
743 | 1 | RTC_HUMCOUNT5_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
744 | 1 | RTC_HUMRH5_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
745 | 1 | RTC_HUMCOUNT6_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
746 | 1 | RTC_HUMRH6_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
747 | 1 | RTC_HUMCOUNT7_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
748 | 1 | RTC_HUMRH7_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
749 | 1 | RTC_HUMCOUNT8_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
750 | 1 | RTC_HUMRH8_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
751 | 1 | RTC_HUMCOUNT9_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
752 | 1 | RTC_HUMRH9_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
753 | 1 | RTC_HUMCOUNT10_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
754 | 1 | RTC_HUMRH10_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
755 | 1 | RTC_HUM_LOCK_A | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
756 | 1 | RTC_HUM_LOCK_B | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
757 | 1 | DISP_ITEM_EXTENAL_SENSOR1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
758 | 1 | DISP_ITEM_EXTENAL_SENSOR2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
759 | 1 | DISP_ITEM_EXTENAL_SENSOR3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
760 | 1 | DISP_ITEM_EXTENAL_SENSOR4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
761 | 1 | EXT_SENSOR_TEMP_CAL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
762 | 1 | BUTTON_LEFT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
763 | 1 | BUTTON_LEFT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
764 | 1 | BUTTON_LEFT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
765 | 1 | BUTTON_LEFT4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
766 | 1 | HUM_HEATING_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
767 | 1 | HUM_INPUT_MANUAL_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
768 | 1 | HUM_INPUT_MANUAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
769 | 1 | CO2_INPUT_MANUAL_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
770 | 1 | CO2_INPUT_MANUAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
771 | 1 | CO2_CALIBRATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CO2 calibration data
772 | 1 | KEYPAD_REVERSE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
773 | 1 | LIGHT_SENSOR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | light sensor value
774 | 1 | PIR_SENSOR_SELECT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
775 | 1 | PIR_SENSOR_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
776 | 1 | PIR_SENSOR_ZERO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
777 | 1 | SPARE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
778 | 1 | PIR_TIMER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
779 | 1 | WIRELESS_PIR_RESPONSE1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
780 | 1 | WIRELESS_PIR_RESPONSE2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
781 | 1 | WIRELESS_PIR_RESPONSE3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
782 | 1 | WIRELESS_PIR_RESPONSE4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
783 | 1 | WIRELESS_PIR_RESPONSE5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
784 | 1 | SPARE1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
785 | 1 | SPARE2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
786 | 1 | TSTAT_HUM_PIC_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
787 | 1 | INTERNAL_SENSOR_MANUAL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0 = AUTO, 1 = MANUAL
788 | 1 | PRESSURE_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
789 | 1 | PRESSURE_MANUAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
790 | 1 | PRESSURE_MANUAL_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
791 | 1 | AQ_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
792 | 1 | AQ_MANUAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
793 | 1 | AQ_MANUAL_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
794 | 1 | TEMPERATURE_OF_PRESSURE_SENSOR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
795 | 1 | TEMPERATURE_OF_HUM_SENSOR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
796 | 1 | SP_DISPLAY_SELECT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
797 | 1 | TSTAT_BK_SN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
798 | 1 | BK_SNLOLO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
799 | 1 | BK_SNLOHI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
800 | 1 | BK_SNHILO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
801 | 1 | UNOCC_AIRFLOW | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
802 | 1 | PWM_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
803 | 1 | SCHEDULE_MODE_NUM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
804 | 1 | TRANSDUCER_RANGE_MIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | When set analog output to transducer mode, use these two reg to set range: range_min = 10 means 0V accodrding to 10C
805 | 1 | TRANSDUCER_RANGE_MAX | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
806 | 1 | ICON_MANUAL_MODE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | manual icons enable/disable 0:auto icon 1: manual icon 2: output control: icon will be on/off depending on outputs state.
807 | 1 | ICON_MANUAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | when set icon to munual mode, set value here
808 | 1 | SOFTWARE_RESET | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
809 | 1 | CO2_SELF_CAL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
810 | 1 | CO2_SELF_CAL_TIME | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
811 | 1 | CO2_SELF_CAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
812 | 1 | CO2_RANGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
813 | 1 | SET_PIR_SENSETIVITY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
814 | 1 | PIR_SPARE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
815 | 1 | MODE1_NAME1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
816 | 1 | MODE1_NAME2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
817 | 1 | MODE1_NAME3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
818 | 1 | MODE1_NAME4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
819 | 1 | MODE2_NAME1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
820 | 1 | MODE2_NAME2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
821 | 1 | MODE2_NAME3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
822 | 1 | MODE2_NAME4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
823 | 1 | MODE3_NAME1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
824 | 1 | MODE3_NAME2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
825 | 1 | MODE3_NAME3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
826 | 1 | MODE3_NAME4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
827 | 1 | MODE4_NAME1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
828 | 1 | MODE4_NAME2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
829 | 1 | MODE4_NAME3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
830 | 1 | MODE4_NAME4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
831 | 1 | MODE5_NAME1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
832 | 1 | MODE5_NAME2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
833 | 1 | MODE5_NAME3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
834 | 1 | MODE5_NAME4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
835 | 1 | OUTSIDETEM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
836 | 1 | OUTSIDETEM_SLAVE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
837 | 1 | TSTAT_TEST1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
838 | 1 | TSTAT_TEST2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
839 | 1 | TSTAT_TEST3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
840 | 1 | TSTAT_TEST4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
841 | 1 | TSTAT_TEST5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
842 | 1 | TSTAT_TEST6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
843 | 1 | TSTAT_TEST7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
844 | 1 | TSTAT_TEST8 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
845 | 1 | TSTAT_TEST9 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
846 | 1 | TSTAT_TEST10 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
847 | 1 | HUM_CALIBRATION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
848 | 1 | PIC_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
849 | 1 | SLEEP_COOLING_DB | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
850 | 1 | SLEEP_HEATING_DB | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
851 | 1 | SLEEP_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
852 | 1 | SLEEP_COOLING_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
853 | 1 | SLEEP_HEATING_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
854 | 1 | MAX_WORK_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | max work setpoint 40C
855 | 1 | MIN_WORK_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | min work setpoint 16C
856 | 1 | MAX_SLEEP_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | max sleeping setpoint 30C
857 | 1 | MIN_SLEEP_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | min sleeping setpoint 15C
858 | 1 | MAX_HOLIDAY_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
859 | 1 | MIN_HOLIDAY_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | min holiday setpoint >5C
860 | 1 | INPUT_VOLTAGE_TERM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
861 | 1 | ICON_DAY_OUTPUT_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
862 | 1 | ICON_NIGHT_OUTPUT_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
863 | 1 | ICON_OCC_OUTPUT_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
864 | 1 | ICON_UNOCC_OUTPUT_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
865 | 1 | ICON_HEAT_OUTPUT_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
866 | 1 | ICON_COOL_OUTPUT_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
867 | 1 | ICON_FAN1_OUTPUT_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
868 | 1 | ICON_FAN2_OUTPUT_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
869 | 1 | ICON_FAN3_OUTPUT_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
870 | 1 | MODBUS_4TO20MA_BOTTOM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
871 | 1 | MODBUS_4TO20MA_TOP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
872 | 1 | MODBUS_4TO20MA_UNIT_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
873 | 1 | MODBUS_4TO20MA_UNIT_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1000 | 1 | SCHEDULE_MONDAY_EVENT1_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | at home (sun + man)
1001 | 1 | SCHEDULE_MONDAY_EVENT1_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1002 | 1 | SCHEDULE_MONDAY_EVENT2_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | at work (sun + no man)
1003 | 1 | SCHEDULE_MONDAY_EVENT2_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1004 | 1 | SCHEDULE_MONDAY_EVENT3_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1005 | 1 | SCHEDULE_MONDAY_EVENT3_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1006 | 1 | SCHEDULE_MONDAY_EVENT4_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1007 | 1 | SCHEDULE_MONDAY_EVENT4_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1008 | 1 | SCHEDULE_MONDAY_EVENT5_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1009 | 1 | SCHEDULE_MONDAY_EVENT5_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1010 | 1 | SCHEDULE_MONDAY_EVENT6_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1011 | 1 | SCHEDULE_MONDAY_EVENT6_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1012 | 1 | SCHEDULE_TUESDAY_EVENT1_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1013 | 1 | SCHEDULE_TUESDAY_EVENT1_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1014 | 1 | SCHEDULE_TUESDAY_EVENT2_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1015 | 1 | SCHEDULE_TUESDAY_EVENT2_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1016 | 1 | SCHEDULE_TUESDAY_EVENT3_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1017 | 1 | SCHEDULE_TUESDAY_EVENT3_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1018 | 1 | SCHEDULE_TUESDAY_EVENT4_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1019 | 1 | SCHEDULE_TUESDAY_EVENT4_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1020 | 1 | SCHEDULE_TUESDAY_EVENT5_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1021 | 1 | SCHEDULE_TUESDAY_EVENT5_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1022 | 1 | SCHEDULE_TUESDAY_EVENT6_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1023 | 1 | SCHEDULE_TUESDAY_EVENT6_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1024 | 1 | SCHEDULE_WENSDAY_EVENT1_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1025 | 1 | SCHEDULE_WENSDAY_EVENT1_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1026 | 1 | SCHEDULE_WENSDAY_EVENT2_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1027 | 1 | SCHEDULE_WENSDAY_EVENT2_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1028 | 1 | SCHEDULE_WENSDAY_EVENT3_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1029 | 1 | SCHEDULE_WENSDAY_EVENT3_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1030 | 1 | SCHEDULE_WENSDAY_EVENT4_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1031 | 1 | SCHEDULE_WENSDAY_EVENT4_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1032 | 1 | SCHEDULE_WENSDAY_EVENT5_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1033 | 1 | SCHEDULE_WENSDAY_EVENT5_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1034 | 1 | SCHEDULE_WENSDAY_EVENT6_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1035 | 1 | SCHEDULE_WENSDAY_EVENT6_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1036 | 1 | SCHEDULE_THURSDAY_EVENT1_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1037 | 1 | SCHEDULE_THURSDAY_EVENT1_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1038 | 1 | SCHEDULE_THURSDAY_EVENT2_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1039 | 1 | SCHEDULE_THURSDAY_EVENT2_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1040 | 1 | SCHEDULE_THURSDAY_EVENT3_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1041 | 1 | SCHEDULE_THURSDAY_EVENT3_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1042 | 1 | SCHEDULE_THURSDAY_EVENT4_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1043 | 1 | SCHEDULE_THURSDAY_EVENT4_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1044 | 1 | SCHEDULE_THURSDAY_EVENT5_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1045 | 1 | SCHEDULE_THURSDAY_EVENT5_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1046 | 1 | SCHEDULE_THURSDAY_EVENT6_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1047 | 1 | SCHEDULE_THURSDAY_EVENT6_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1048 | 1 | SCHEDULE_FRIDAY_EVENT1_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1049 | 1 | SCHEDULE_FRIDAY_EVENT1_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1050 | 1 | SCHEDULE_FRIDAY_EVENT2_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1051 | 1 | SCHEDULE_FRIDAY_EVENT2_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1052 | 1 | SCHEDULE_FRIDAY_EVENT3_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1053 | 1 | SCHEDULE_FRIDAY_EVENT3_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1054 | 1 | SCHEDULE_FRIDAY_EVENT4_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1055 | 1 | SCHEDULE_FRIDAY_EVENT4_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1056 | 1 | SCHEDULE_FRIDAY_EVENT5_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1057 | 1 | SCHEDULE_FRIDAY_EVENT5_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1058 | 1 | SCHEDULE_FRIDAY_EVENT6_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1059 | 1 | SCHEDULE_FRIDAY_EVENT6_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1060 | 1 | SCHEDULE_SATDAY_EVENT1_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1061 | 1 | SCHEDULE_SATDAY_EVENT1_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1062 | 1 | SCHEDULE_SATDAY_EVENT2_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1063 | 1 | SCHEDULE_SATDAY_EVENT2_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1064 | 1 | SCHEDULE_SATDAY_EVENT3_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1065 | 1 | SCHEDULE_SATDAY_EVENT3_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1066 | 1 | SCHEDULE_SATDAY_EVENT4_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1067 | 1 | SCHEDULE_SATDAY_EVENT4_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1068 | 1 | SCHEDULE_SATDAY_EVENT5_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1069 | 1 | SCHEDULE_SATDAY_EVENT5_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1070 | 1 | SCHEDULE_SATDAY_EVENT6_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1071 | 1 | SCHEDULE_SATDAY_EVENT6_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1072 | 1 | SCHEDULE_SUNDAY_EVENT1_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1073 | 1 | SCHEDULE_SUNDAY_EVENT1_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1074 | 1 | SCHEDULE_SUNDAY_EVENT2_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1075 | 1 | SCHEDULE_SUNDAY_EVENT2_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1076 | 1 | SCHEDULE_SUNDAY_EVENT3_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1077 | 1 | SCHEDULE_SUNDAY_EVENT3_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1078 | 1 | SCHEDULE_SUNDAY_EVENT4_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1079 | 1 | SCHEDULE_SUNDAY_EVENT4_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1080 | 1 | SCHEDULE_SUNDAY_EVENT5_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1081 | 1 | SCHEDULE_SUNDAY_EVENT5_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1082 | 1 | SCHEDULE_SUNDAY_EVENT6_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1083 | 1 | SCHEDULE_SUNDAY_EVENT6_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1084 | 1 | SCHEDULE_HOLIDAY_EVENT1_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1085 | 1 | SCHEDULE_HOLIDAY_EVENT1_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1086 | 1 | SCHEDULE_HOLIDAY_EVENT2_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1087 | 1 | SCHEDULE_HOLIDAY_EVENT2_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1088 | 1 | SCHEDULE_HOLIDAY_EVENT3_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1089 | 1 | SCHEDULE_HOLIDAY_EVENT3_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1090 | 1 | SCHEDULE_HOLIDAY_EVENT4_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1091 | 1 | SCHEDULE_HOLIDAY_EVENT4_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1092 | 1 | SCHEDULE_HOLIDAY_EVENT5_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1093 | 1 | SCHEDULE_HOLIDAY_EVENT5_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1094 | 1 | SCHEDULE_HOLIDAY_EVENT6_H | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1095 | 1 | SCHEDULE_HOLIDAY_EVENT6_M | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1096 | 1 | SCHEDULE_MONDAY_FLAG_1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1097 | 1 | SCHEDULE_MONDAY_FLAG_2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1098 | 1 | SCHEDULE_TUESDAY_FLAG_1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1099 | 1 | SCHEDULE_TUESDAY_FLAG_2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1100 | 1 | SCHEDULE_WENSDAY_FLAG_1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1101 | 1 | SCHEDULE_WENSDAY_FLAG_2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1102 | 1 | SCHEDULE_THURSDAY_FLAG_1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1103 | 1 | SCHEDULE_THURSDAY_FLAG_2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1104 | 1 | SCHEDULE_FRIDAY_FLAG_1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1105 | 1 | SCHEDULE_FRIDAY_FLAG_2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1106 | 1 | SCHEDULE_SATDAY_FLAG_1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1107 | 1 | SCHEDULE_SATDAY_FLAG_2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1108 | 1 | SCHEDULE_SUNDAY_FLAG_1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1109 | 1 | SCHEDULE_SUNDAY_FLAG_2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1110 | 1 | SCHEDULE_HOLIDAY_FLAG_1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1111 | 1 | SCHEDULE_HOLIDAY_FLAG_2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1112 | 1 | SCHEDULE_DAY_BEGAIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1158 | 1 | SCHEDULE_DAY_END | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1159 | 1 | AWAY_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1160 | 1 | AWAY_COOLING_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1161 | 1 | AWAY_HEATING_SP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1162 | 1 | AWAY_COOL_DB | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1163 | 1 | AWAY_HEAT_DB | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1164 | 1 | BACNET_STATION_NUM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1165 | 1 | BACNET_INSTANCE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1166 | 1 | BAC_T1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1167 | 1 | BAC_T2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1168 | 1 | BAC_T3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1169 | 1 | BAC_T4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1170 | 1 | BAC_T5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1171 | 1 | BAC_T6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1172 | 1 | BAC_T7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
1173 | 1 | BAC_T8 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
2000 | 1 | FRC_ENABLE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | free cooling function enable/disable 0:DIABLE 1:ENABLE
2001 | 1 | FRC_BASE_SELECT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING BASE SELECT 0: TEMPERATUERE BASE 1: ENTHALPY BASE
2002 | 1 | FRC_SPACETEM_SOURCE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING SPACE TEMPERATURE SOURCE SELECT, INTERNAL OR NETWORK
2003 | 1 | FRC_SPACETEM_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CURRENT SPACE TEMPERATURE
2004 | 1 | FRC_SPACETEM_UNIT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | SPACE TEMPERATURE UNIT
2005 | 1 | FRC_SPACETEM_ID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | if internal sensor COULD BE INTERNAL SENSOR, AI1 TO AI8 OR GET FROM NETWORK if remote sensor, this is pannel number
2006 | 1 | FRC_SPACETEM_LASTUPDATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING SPACE TEMPERATURE LAST UPDATE TIME, UNIT: MINUTS
2007 | 1 | FRC_SPACETEM_STATUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CHECK IF SPACE TEMPERATURE SOURCE IS WORK WELL
2008 | 1 | FRC_SPACETEM_CONFIG | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING SPACE TEMPERATURE STATUS, CHECK RANGE,UNIT
2009 | 1 | FRC_SUPPLYTEM_SOURCE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING SUPPLY TEMPERATURE SOURCE SELECT, INTERNAL OR NETWORK
2010 | 1 | FRC_SUPPLYTEM_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CURRENT SUPPLYTEM TEMPERATURE
2011 | 1 | FRC_SUPPLYTEM_UNIT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | SUPPLYTEM TEMPERATURE UNIT
2012 | 1 | FRC_SUPPLYTEM_ID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | COULD BE INTERNAL SENSOR, AI1 TO AI8 OR GET FROM NETWORK
2013 | 1 | FRC_SUPPLYTEM_LASTUPDATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING SUPPLY TEMPERATURE LAST UPDATE TIME, UNIT: MINUTS
2014 | 1 | FRC_SUPPLYTEM_STATUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CHECK IF SUPPLY TEMPERATURE SOURCE IS WORK WELL
2015 | 1 | FRC_SUPPLYTEM_CONFIG | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING SUPPLY TEMPERATURE STATUS, CHECK RANGE,UNIT
2016 | 1 | FRC_OUTDOORTEM_SOURCE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING OUTDOOR TEMPERATURE SOURCE SELECT, INTERNAL OR NETWORK
2017 | 1 | FRC_OUTDOORTEM_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CURRENT OUTDOORTEM TEMPERATURE
2018 | 1 | FRC_OUTDOORTEM_UNIT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | OUTDOORTEM TEMPERATURE UNIT
2019 | 1 | FRC_OUTDOORTEM_ID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | COULD BE INTERNAL SENSOR, AI1 TO AI8 OR GET FROM NETWORK
2020 | 1 | FRC_OUTDOORTEM_LASTUPDATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING OUTDOOR TEMPERATURE LAST UPDATE TIME, UNIT: MINUTS
2021 | 1 | FRC_OUTDOORTEM_STATUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CHECK IF OUTDOOR TEMPERATURE SOURCE IS WORK WELL
2022 | 1 | FRC_OUTDOORTEM_CONFIG | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING OUTDOOR TEMPERATURE STATUS, CHECK RANGE,UNIT
2023 | 1 | FRC_INDOORHUM_SOURCE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING INDOOR HUMIDITY SOURCE SELECT, INTERNAL OR NETWORK
2024 | 1 | FRC_INDOORHUM_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CURRENT INDOOR HUM
2025 | 1 | FRC_INDOORHUM_UNIT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INDOO RHUM UNIT
2026 | 1 | FRC_INDOORHUM_ID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | COULD BE INTERNAL SENSOR, AI1 TO AI8 OR GET FROM NETWORK
2027 | 1 | FRC_INDOORHUM_LASTUPDATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING OUTDOOR HUMIDITY LAST UPDATE TIME, UNIT: MINUTS
2028 | 1 | FRC_INDOORHUM_STATUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CHECK IF INDOOR HUMIDITY SOURCE IS WORK WELL
2029 | 1 | FRC_INDOORHUM_CONFIG | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING INDOOR HUMIDITY STATUS, CHECK RANGE,UNIT
2030 | 1 | FRC_OUTDOORHUM_SOURCE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING OUTDOOR HUMIDITY SOURCE SELECT, INTERNAL OR NETWORK
2031 | 1 | FRC_OUTDOORHUM_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CURRENT OUTDOOR HUM
2032 | 1 | FRC_OUTDOORHUM_UNIT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | OUTDOOR RHUM UNIT
2033 | 1 | FRC_OUTDOORHUM_ID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | COULD BE INTERNAL SENSOR, AI1 TO AI8 OR GET FROM NETWORK
2034 | 1 | FRC_OUTDOORHUM_LASTUPDATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING OUTDOOR HUMIDITY LAST UPDATE TIME, UNIT: MINUTS
2035 | 1 | FRC_OUTDOORHUM_STATUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CHECK IF OUTDOOR HUMIDITY SOURCE IS WORK WELL
2036 | 1 | FRC_OUTDOORHUM_CONFIG | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING OUTDOOR HUMIDITY STATUS, CHECK RANGE,UNIT
2037 | 1 | FRC_MIN_FRESH_AIR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | MINIMAL FRESH AIR, UNIT PERCENTAGE 0-100%
2038 | 1 | FRC_MIN_FRESH_AIRTEM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | MINIMAL FRESH AIR TEMPERATURE, UNIT DEGREE C/F
2039 | 1 | FRC_OUTPUT_SELECT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
2040 | 1 | FRC_OUTPUT_CONFIG | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING OUTPUT CHECK, OUTPUT SOURCE, OUTPUT FUNCTION
2041 | 1 | FRC_PID2_CONFIG | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | FREE COOLING PID2 CONFIG CHECK, CHECK IF PID2 HAS INPUT FROM SUPPLY SENSOR, ALSO CHECK IF IT IS SET TO NEGATIVE COOLING
2042 | 1 | FRC_OUTPUT_MODE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | SET FAN TO OFF
2043 | 1 | FRC_TOTAL_CONFIG | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1045 MINIMAL SUPPLY AIR TEMPERATURE UNIT: DEGREE C/F
2044 | 1 | FRC_PRESENT_MODE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
2045 | 1 | FRC_OUTDOOR_ENTHALPY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
2046 | 1 | FRC_INDOOR_ENTHALPY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
2047 | 1 | FRC_PID2_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
11748 |  | FRC_SPACETEM_STR_BEGAIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
11771 |  | FRC_SPACETEM_STR_END | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
11772 |  | FRC_SUPPLYTEM_STR_BEGAIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
11795 |  | FRC_SUPPLYTEM_STR_END | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
11796 |  | FRC_OUTDOORTEM_STR_BEGAIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
11819 |  | FRC_OUTDOORTEM_STR_END | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
11820 |  | FRC_INDOORHUM_STR_BEGAIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
11843 |  | FRC_INDOORHUM_STR_END | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
11844 |  | FRC_OUTDOORHUM_BEGAIN | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
11867 |  | FRC_OUTDOORHUM_END | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer

## CO2_Node
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI
4 | 2 | MODBUS_VERSION_NUMBER_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Software Version – 2 byte value. Read-only
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | ADDRESS. Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Product Model. This is a read-only register that is used by the microcontroller to determine the product
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | [INVALID_DATA]
9 | 1 | MODBUS_PIC_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIC firmware version
10 | 1 | MODBUS_HUM_PIC_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIC version of Humidity module
11 | 1 | MODBUS_ADDRESS_PLUG_N_PLAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | [INVALID_DATA]
15 | 1 | MODBUS_BASE_ADDRESS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
16 | 1 | MODBUS_UPDATE_STATUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Firmware Update Register, used to show the status of firmware updates.Writing 143 sets the config back to out of the box except for Modbus ID and baud rate. Write 159 to fix the current config as the user defaults, this is done automatically by T3000 any
21 | 1 | MODBUS_PROTOCOL_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Porotocol of communication, 3 for modbus, 0 for BACnet MSTP
37 | 2 | MODBUS_INSTANCE | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer LO_HI | BACnet instance
39 | 1 | MODBUS_INSTANCE_LOWORD | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | BACnet station number
100 | 1 | MODBUS_AD_OUTPUT_VF_CO2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Voltage feedback of CO2
101 | 1 | MODBUS_AD_OUTPUT_VF_TEMP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Voltage feedback of temperature
102 | 1 | MODBUS_AD_OUTPUT_VF_HUM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Voltage feedback of humidity
103 | 1 | MODBUS_AD_OUTPUT_IF_CO2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Current feedback of CO2
104 | 1 | MODBUS_AD_OUTPUT_IF_TEMP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Current feedback of temperature
105 | 1 | MODBUS_AD_OUTPUT_IF_HUM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Current feedback of humidity
106 | 1 | MODBUS_AD_THERMISTOR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | adc value of on board thermistor sensor, read only
107 | 1 | MODBUS_PIC_AD_LIGHTING | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | adc value of on board light sensor, read only
108 | 1 | MODBUS_CO2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | co2 value (ppm). It will be calibrated if write to it.
109 | 1 | MODBUS_CO2_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | co2 calibration offset. User can change it to calibrate the co2 ppm. It will be changed also if user write the data to register co2 ppm
110 | 1 | MODBUS_CO2_SLOPE_DETECT_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Delta value for eliminating the pulse ppm value. The default value is 200.
111 | 1 | MODBUS_CO2_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Fitler times, make the ppm value go smooth. The default value is 5.
112 | 1 | MODBUS_CO2_PRE_ALARM_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The fair alarm ppm setpoint of co2 sensor.
113 | 1 | MODBUS_CO2_ALARM_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The poor alarm ppm setpoint of co2 sensor.
114 | 1 | MODBUS_ALARM_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | co2 alarm status:0b'xxxx 1xxx': co2 poor;0b'xxxx 01xx': co2 fair;0b'xxxx 001x': co2 good
115 | 1 | MODBUS_HUMIDITY_VERSION | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | the version number of humidity sensor
116 | 1 | MODBUS_HUMIDITY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the relative humidity
117 | 1 | MODBUS_HUMIDITY_FILTER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | the frequency value read from humidity sensor, read only
118 | 1 | MODBUS_HUMIDITY_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the number of calibration points of the humidity sensor
119 | 1 | MODBUS_HUMIDITY_TEMP_C | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | degree celsius temperature value of the humidity sensor
120 | 1 | MODBUS_HUMIDITY_TEMP_F | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | degree fahrenheit temperature value of the humidity sensor
121 | 1 | MODBUS_INTERNAL_TEMP_C | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | celsius degree temperature value of the on board thermistor sensor
122 | 1 | MODBUS_TEMPERATURE_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | fahrenheit degree temperature value of the on board thermistor sensor
123 | 1 | MODBUS_TEMPERATURE_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the offset for calibrating the on board thermistor sensor
124 | 1 | MODBUS_TEMPERATURE_DSELECT | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | select the temperature direct to analog output:0: on board thermistor sensor, default setting;1: humidity sensor
125 | 1 | MODBUS_TEMPERATURE_DEGREE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | select the temperature unit direct to analog output:0: degree celsius;1: degree fahrenheit, default setting
126 | 1 | MODBUS_LIGHTING | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Lighting value, for feature
127 | 1 | MODBUS_OUTPUT_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog output mode, change it by setting the jumper (J20) on the board, read only
128 | 1 | MODBUS_OUTPUT_RANGE_MIN_TEM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the minimum value of temperature directs to the analog output
129 | 1 | MODBUS_OUTPUT_RANGE_MAX_TEM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the maximum value of temperature directs to the analog output
130 | 1 | MODBUS_OUTPUT_RANGE_MIN_HUM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the minimum value of humidity directs to the analog output
131 | 1 | MODBUS_OUTPUT_RANGE_MAX_HUM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the maximum value of humidity directs to the analog output
132 | 1 | MODBUS_OUTPUT_RANGE_MIN_CO2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the minimum value of co2 directs to the analog output
133 | 1 | MODBUS_OUTPUT_RANGE_MAX_CO2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the maximum value of co2 directs to the analog output
134 | 1 | MODBUS_AUTO_MANUAL | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog output auto/manual control. Bit 0 directs to co2 output, Bit 1 directs to temperature output, Bit 2 directs to humidity output. 0=Auto, 1=Manual.
135 | 1 | MODBUS_CO2_MANUAL_VAL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The manual value of co2.
136 | 1 | MODBUS_TEMP_MANUAL_VAL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The manual value of temperature.
137 | 1 | MODBUS_HUM_MANUAL_VAL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The manual value of humidity.
138 | 1 | MODBUS_AD_OUTPUT_FB_CO2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
139 | 1 | MODBUS_AD_OUTPUT_FB_TEMP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
140 | 1 | MODBUS_AD_OUTPUT_FB_HUM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
141 | 1 | MODBUS_OUTPUT_CO2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
142 | 1 | MODBUS_OUTPUT_TEMP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
143 | 1 | MODBUS_OUTPUT_HUM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
144 | 1 | MODBUS_OUTPUT_HUM_VOL_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
145 | 1 | MODBUS_OUTPUT_TEMP_VOL_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
146 | 1 | MODBUS_OUTPUT_CO2_VOL_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
147 | 1 | MODBUS_OUTPUT_HUM_CUR_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
148 | 1 | MODBUS_OUTPUT_TEMP_CUR_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
149 | 1 | MODBUS_OUTPUT_CO2_CUR_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
150 | 1 | MODBUS_CO2_INTERNAL_EXIST | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Internal CO2 sensor selection. The value is 1 as default. 1 = MAYBE_OGM200;2=MAYBE_TEMCO_CO2;3=OGM200;4=TEMCO_CO2.
151 | 1 | MODBUS_READ_CO2_CTR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
152 | 1 | MODBUS_PASSWORD_ENABLE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Enable/Disable the password for the menu system operation. 0=Disable, 1=Enable.
153 | 1 | MODBUS_USER_PASSWORD0 | 03_06 Read Holding and Write Single | Character String HI_LO | The first digital of the password. Should be from 0 to 9.
154 | 1 | MODBUS_USER_PASSWORD1 | 03_06 Read Holding and Write Single | Character String HI_LO | The second digital of the password. Should be from 0 to 9.
155 | 1 | MODBUS_USER_PASSWORD2 | 03_06 Read Holding and Write Single | Character String HI_LO | The third digital of the password. Should be from 0 to 9.
156 | 1 | MODBUS_USER_PASSWORD3 | 03_06 Read Holding and Write Single | Character String HI_LO | The fourth digital of the password. Should be from 0 to 9.
157 | 1 | MODBUS_MENU_BLOCK_SECONDS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
158 | 1 | MODBUS_BACKLIGHT_KEEP_SECONDS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
159 | 1 | MODBUS_REPLY_DELAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Modbus reply delay time (ms)
160 | 1 | MODBUS_RECEIVE_DELAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Modbus receive delay time(ms)
161 | 1 | MODBUS_DEW_PT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
162 | 1 | MODBUS_DEW_PT_F | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
163 | 1 | MODBUS_PWS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
164 | 1 | MODBUS_MIX_RATIO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
165 | 1 | MODBUS_ENTHALPY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
166 | 1 | MODBUS_CO2_SP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
167 | 1 | MODBUS_TEMP_SP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
168 | 1 | MODBUS_HUM_SP | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
169 | 1 | MODBUS_DIS_ITERM | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | bit0:T, bit1:H, bit2:co2, bit3:Td, bit4:T_SP, bit5:H_SP, bit6 CO2_SP bit7 user message(two lines) bit8 AQ
170 | 1 | MODBUS_SCROLL_SET | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | bit0:rx/tx,bit1:alarm,bit2:CO2 status,bit3:T, bit4:H, bit5:co2, bit6:Td, bit7:T_SP, bit8:H_SP, bit9 CO2_SP bit10 outdoor tem bit11 user message.
171 | 1 | MODBUS_DIS_BLOCK_SECONDS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
172 | 1 | MODBUS_TEMP_SP_MIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
173 | 1 | MODBUS_TEMP_SP_MAX | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
174 | 1 | MODBUS_HUM_SP_MIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
175 | 1 | MODBUS_HUM_SP_MAX | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
176 | 1 | MODBUS_CO2_SP_MIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
177 | 1 | MODBUS_CO2_SP_MAX | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
178 | 1 | MODBUS_DIS_SP_NUM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | bit0: temperature bit1:hum bit2 co2
179 | 1 | MODBUS_ADJUST_SPEED | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
180 | 1 | MODBUS_OUTDOOR_TEM_ENABLE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0:DIABLE 1:ENABLE
181 | 1 | MODBUS_OUTDOOR_TEM_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
182 | 1 | MODBUS_CO2_TEST1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
183 | 1 | MODBUS_CO2_TEST2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
184 | 1 | MODBUS_AQ_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
185 | 1 | MODBUS_CELBRA_AIR1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
186 | 1 | MODBUS_CELBRA_AIR2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
187 | 1 | MODBUS_CELBRA_AIR3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
188 | 1 | MODBUS_CELBRA_AIR4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
189 | 1 | MODBUS_AQ_LEVEL0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
190 | 1 | MODBUS_AQ_LEVEL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
191 | 1 | MODBUS_AQ_LEVEL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
192 | 1 | MODBUS_MAX_AQ_VAL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
193 | 1 | MODBUS_CALIBRATION_AQ | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
500 | 1 | MODBUS_CO2_BKCAL_ONOFF | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | co2 automatic compensation background enalbe or disable.0 = Disable,1= Enable
501 | 1 | MODBUS_CO2_NATURE_LEVEL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | “Background C02”, default is 400ppm, minimum is 390, max is 500.
502 | 1 | MODBUS_CO2_MIN_ADJ | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Maximum adjustment per day” default is 1ppm, max is 10 ppm, minimum is 1
503 | 1 | MODBUS_CO2_CAL_DAYS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | “Number of days to watch for minimum” , default is 7 days. Max is 30 days. Minimum is 2 days.
504 | 1 | MODBUS_CO2_LOWVALUE_REMAIN_TIME | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | co2 background calibration offset
505 | 1 | MODBUS_CO2_BKCAL_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer

## T38I8O6DO
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
11 | 1 | MODBUS_ISP_VERSION | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | bootloader revision
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | baudrate 0=9600,1=19200,2=38400,3=57600,4=115200,5=76800
21 | 1 | MODBUS_PROTOCOL_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | protocal type. 0=mstp, 3=modbus
22 | 2 | MODBUS_INSTANCE_HIGH | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | high word of instance
23 | 2 | MODBUS_INSTANCE_LOW | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | low word of instance
30 | 1 | MODBUS_OUTPUT_DEAD_MASTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | dead master of outputs
37 | 1 | MODBUS_MAX_MASTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
38 | 1 | MODBUS_BACNET_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
39 | 1 | MODBUS_STATION_NUM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
40 | 6 | MODBUS_MAC | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC address
46 | 1 | MODBUS_IP_MODE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | IP mode. 0=static IP; 1= DHCP
47 | 1 | MODBUS_IP_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
48 | 1 | MODBUS_IP_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
49 | 1 | MODBUS_IP_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
50 | 1 | MODBUS_IP_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
51 | 1 | MODBUS_SUBNET_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
52 | 1 | MODBUS_SUBNET_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
53 | 1 | MODBUS_SUBNET_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
54 | 1 | MODBUS_SUBNET_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
55 | 1 | MODBUS_GETWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
56 | 1 | MODBUS_GETWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
57 | 1 | MODBUS_GETWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
58 | 1 | MODBUS_GETWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
59 | 1 | MODBUS_TCPSERVER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0,TCP server
60 | 1 | MODBUS_TCP_LISTEN_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | listen port at TCP server mode
61 | 1 | MODBUS_GHOST_IP_MODE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Ghost IP mode. 0=static IP; 1= DHCP
62 | 1 | MODBUS_GHOST_IP_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
63 | 1 | MODBUS_GHOST_IP_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
64 | 1 | MODBUS_GHOST_IP_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
65 | 1 | MODBUS_GHOST_IP_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
66 | 1 | MODBUS_GHOST_SUBNET_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
67 | 1 | MODBUS_GHOST_SUBNET_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
68 | 1 | MODBUS_GHOST_SUBNET_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
69 | 1 | MODBUS_GHOST_SUBNET_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
70 | 1 | MODBUS_GHOST_GETWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
71 | 1 | MODBUS_GHOST_GETWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
72 | 1 | MODBUS_GHOST_GETWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
73 | 1 | MODBUS_GHOST_GETWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
74 | 1 | MODBUS_GHOST_TCPSERVER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0,TCP server
75 | 1 | MODBUS_GHOST_TCP_LISTEN_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | listen port at TCP server mode
76 | 1 | MODBUS_WRITE_GHOST_SYSTEM | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
80 | 1 | MODBUS_REPOWER_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | output resume to OFF or last status
90 | 1 | MODBUS_BACNET_VENDOR_ID | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
93 | 1 | MODBUS_MAC_ENABLE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
99 | 1 | MODBUS_SERINALNUMBER_WRITE_FLAG | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
100 | 1 | MODBUS_AO_CHANNLE0 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | analog output1
101 | 1 | MODBUS_AO_CHANNLE1 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | analog output2
102 | 1 | MODBUS_AO_CHANNLE2 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | analog output3
103 | 1 | MODBUS_AO_CHANNLE3 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | analog output4
104 | 1 | MODBUS_AO_CHANNLE4 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | analog output5
105 | 1 | MODBUS_AO_CHANNLE5 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | analog output6
106 | 1 | MODBUS_AO_CHANNLE6 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | analog output7
107 | 1 | MODBUS_AO_CHANNLE7 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | analog output8
108 | 1 | MODBUS_DO_CHANNLE0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit output1
109 | 1 | MODBUS_DO_CHANNLE1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit output2
110 | 1 | MODBUS_DO_CHANNLE2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit output3
111 | 1 | MODBUS_DO_CHANNLE3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit output4
112 | 1 | MODBUS_DO_CHANNLE4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit output5
113 | 1 | MODBUS_DO_CHANNLE5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit output6
116 | 2 | MODBUS_AI_CHANNLE0 | 03_06 Read Holding and Write Single | Floating HI_LO/1000
118 | 2 | MODBUS_AI_CHANNLE1 | 03_06 Read Holding and Write Single | Floating HI_LO/1000
120 | 2 | MODBUS_AI_CHANNLE2 | 03_06 Read Holding and Write Single | Floating HI_LO/1000
122 | 2 | MODBUS_AI_CHANNLE3 | 03_06 Read Holding and Write Single | Floating HI_LO/1000
124 | 2 | MODBUS_AI_CHANNLE4 | 03_06 Read Holding and Write Single | Floating HI_LO/1000
126 | 2 | MODBUS_AI_CHANNLE5 | 03_06 Read Holding and Write Single | Floating HI_LO/1000
128 | 2 | MODBUS_AI_CHANNLE6 | 03_06 Read Holding and Write Single | Floating HI_LO/1000
130 | 2 | MODBUS_AI_CHANNLE7 | 03_06 Read Holding and Write Single | Floating HI_LO/1000
140 | 1 | MODBUS_AI_CHANNEL_JUMP0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | jumper setting for input0
141 | 1 | MODBUS_AI_CHANNEL_JUMP1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | jumper setting for input1
142 | 1 | MODBUS_AI_CHANNEL_JUMP2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | jumper setting for input2
143 | 1 | MODBUS_AI_CHANNEL_JUMP3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | jumper setting for input3
144 | 1 | MODBUS_AI_CHANNEL_JUMP4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | jumper setting for input4
145 | 1 | MODBUS_AI_CHANNEL_JUMP5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | jumper setting for input5
146 | 1 | MODBUS_AI_CHANNEL_JUMP6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | jumper setting for input6
147 | 1 | MODBUS_AI_CHANNEL_JUMP7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | jumper setting for input7
149 | 1 | MODBUS_AUTO_MANUAL0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for input0
150 | 1 | MODBUS_AUTO_MANUAL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for input1
151 | 1 | MODBUS_AUTO_MANUAL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for input2
152 | 1 | MODBUS_AUTO_MANUAL3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for input3
153 | 1 | MODBUS_AUTO_MANUAL4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for input4
154 | 1 | MODBUS_AUTO_MANUAL5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for input5
155 | 1 | MODBUS_AUTO_MANUAL6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for input6
156 | 1 | MODBUS_AUTO_MANUAL7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for input7
157 | 1 | MODBUS_AI_DI_AI0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit and analog setting for input0
158 | 1 | MODBUS_AI_DI_AI1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit and analog setting for input1
159 | 1 | MODBUS_AI_DI_AI2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit and analog setting for input2
160 | 1 | MODBUS_AI_DI_AI3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit and analog setting for input3
161 | 1 | MODBUS_AI_DI_AI4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit and analog setting for input4
162 | 1 | MODBUS_AI_DI_AI5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit and analog setting for input5
163 | 1 | MODBUS_AI_DI_AI6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit and analog setting for input6
164 | 1 | MODBUS_AI_DI_AI7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | digit and analog setting for input7
165 | 1 | MODBUS_CAL_SIGN0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate sign for input0
166 | 1 | MODBUS_CAL_SIGN1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate sign for input1
167 | 1 | MODBUS_CAL_SIGN2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate sign for input2
168 | 1 | MODBUS_CAL_SIGN3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate sign for input3
169 | 1 | MODBUS_CAL_SIGN4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate sign for input4
170 | 1 | MODBUS_CAL_SIGN5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate sign for input5
171 | 1 | MODBUS_CAL_SIGN6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate sign for input6
172 | 1 | MODBUS_CAL_SIGN7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate sign for input7
173 | 2 | MODBUS_CAL_VALUE0 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input0
175 | 2 | MODBUS_CAL_VALUE1 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input1
177 | 2 | MODBUS_CAL_VALUE2 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input2
179 | 2 | MODBUS_CAL_VALUE3 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input3
181 | 2 | MODBUS_CAL_VALUE4 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input4
183 | 2 | MODBUS_CAL_VALUE5 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input5
185 | 2 | MODBUS_CAL_VALUE6 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input6
187 | 2 | MODBUS_CAL_VALUE7 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input7
189 | 1 | MODBUS_AI_STATUS_0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for input0
190 | 1 | MODBUS_AI_STATUS_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for input1
191 | 1 | MODBUS_AI_STATUS_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for input2
192 | 1 | MODBUS_AI_STATUS_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for input3
193 | 1 | MODBUS_AI_STATUS_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for input4
194 | 1 | MODBUS_AI_STATUS_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for input5
195 | 1 | MODBUS_AI_STATUS_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for input6
196 | 1 | MODBUS_AI_STATUS_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for input7
200 | 1 | MODBUS_AI_FILTER0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | filter value for input0
201 | 1 | MODBUS_AI_FILTER1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | filter value for input1
202 | 1 | MODBUS_AI_FILTER2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | filter value for input2
203 | 1 | MODBUS_AI_FILTER3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | filter value for input3
204 | 1 | MODBUS_AI_FILTER4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | filter value for input4
205 | 1 | MODBUS_AI_FILTER5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | filter value for input5
206 | 1 | MODBUS_AI_FILTER6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | filter value for input6
207 | 1 | MODBUS_AI_FILTER7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | filter value for input7
225 | 1 | MODBUS_AI_RANGE0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 0 range. if analog inputs (not_used_input = 0, Y3K_40_150DegC = 1, Y3K_40_300DegF, R10K_40_120DegC, R10K_40_250DegF, R3K_40_150DegC, R3K_40_300DegF, KM10K_40_120DegC, KM10K_40_250DegF, A10K_50_110DegC, A10K_60_200DegF, V0_5, I0_100Amps, I0_20ma, I0_20psi, N0_2_32counts, N0_3000FPM_0_5V, P0_100_0_5V, P0_100_4_20ma, P0_255p_min, table1, table2, table3, table4, table5,100 - HI_SPEED_COUNTER ), if digital inputs(not_used_input = 0,OFF_ON, CLOSED_OPEN, STOP_START, DISABLED_ENABLED, NORMAL_ALARM, NORMAL_HIGH, NORMAL_LOW, NO_YES, COOL_HEAT, UNOCCUPIED_OCCUPIED, LOW_HIGH, ON_OFF , OPEN_CLOSED, START_STOP, ENABLED_DISABLED, ALARM_NORMAL, HIGH_NORMAL, LOW_NORMAL, YES_NO, HEAT_COOL, OCCUPIED_UNOCCUPIED, HIGH_LOW, custom_digital1, custom_digital2, custom_digital3, custom_digital4, custom_digital5, custom_digital6, custom_digital7, custom_digital8 )
226 | 1 | MODBUS_AI_RANGE1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | range value for input1
227 | 1 | MODBUS_AI_RANGE2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | range value for input2
228 | 1 | MODBUS_AI_RANGE3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | range value for input3
229 | 1 | MODBUS_AI_RANGE4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | range value for input4
230 | 1 | MODBUS_AI_RANGE5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | range value for input5
231 | 1 | MODBUS_AI_RANGE6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | range value for input6
232 | 1 | MODBUS_AI_RANGE7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | range value for input7
240 | 1 | MODBUS_AUTO_MANUAL_OUT0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output0
241 | 1 | MODBUS_AUTO_MANUAL_OUT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output1
242 | 1 | MODBUS_AUTO_MANUAL_OUT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output2
243 | 1 | MODBUS_AUTO_MANUAL_OUT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output3
244 | 1 | MODBUS_AUTO_MANUAL_OUT4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output4
245 | 1 | MODBUS_AUTO_MANUAL_OUT5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output5
246 | 1 | MODBUS_AUTO_MANUAL_OUT6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output6
247 | 1 | MODBUS_AUTO_MANUAL_OUT7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output7
248 | 1 | MODBUS_AUTO_MANUAL_OUT8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output8
249 | 1 | MODBUS_AUTO_MANUAL_OUT9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output9
250 | 1 | MODBUS_AUTO_MANUAL_OUT10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output10
251 | 1 | MODBUS_AUTO_MANUAL_OUT11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output11
252 | 1 | MODBUS_AUTO_MANUAL_OUT12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output12
253 | 1 | MODBUS_AUTO_MANUAL_OUT13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | auto manual setting for output13
254 | 1 | MODBUS_OUTPUT_STATUS_0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs0
255 | 1 | MODBUS_OUTPUT_STATUS_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs1
256 | 1 | MODBUS_OUTPUT_STATUS_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs2
257 | 1 | MODBUS_OUTPUT_STATUS_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs3
258 | 1 | MODBUS_OUTPUT_STATUS_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs4
259 | 1 | MODBUS_OUTPUT_STATUS_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs5
260 | 1 | MODBUS_OUTPUT_STATUS_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs6
261 | 1 | MODBUS_OUTPUT_STATUS_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs7
262 | 1 | MODBUS_OUTPUT_STATUS_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs8
263 | 1 | MODBUS_OUTPUT_STATUS_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs9
264 | 1 | MODBUS_OUTPUT_STATUS_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs10
265 | 1 | MODBUS_OUTPUT_STATUS_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs11
266 | 1 | MODBUS_OUTPUT_STATUS_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs12
267 | 1 | MODBUS_OUTPUT_STATUS_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | status for outputs13
268 | 1 | MODBUS_OUTPUT_RANGE_0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | high bye is analog or digital (digital is 0, analog is 1), low byte is range. if analog inputs (not_used_input = 0, Y3K_40_150DegC, Y3K_40_300DegF, R10K_40_120DegC, R10K_40_250DegF, R3K_40_150DegC, R3K_40_300DegF, KM10K_40_120DegC, KM10K_40_250DegF, A10K_50_110DegC, A10K_60_200DegF, V0_5, I0_100Amps, I0_20ma, I0_20psi, N0_2_32counts, N0_3000FPM_0_5V, P0_100_0_5V, P0_100_4_20ma, P0_255p_min, table1, table2, table3, table4, table5,100 - HI_SPEED_COUNTER ), if digital inputs(not_used_input = 0,OFF_ON, CLOSED_OPEN, STOP_START, DISABLED_ENABLED, NORMAL_ALARM, NORMAL_HIGH, NORMAL_LOW, NO_YES, COOL_HEAT, UNOCCUPIED_OCCUPIED, LOW_HIGH, ON_OFF , OPEN_CLOSED, START_STOP, ENABLED_DISABLED, ALARM_NORMAL, HIGH_NORMAL, LOW_NORMAL, YES_NO, HEAT_COOL, OCCUPIED_UNOCCUPIED, HIGH_LOW, custom_digital1, custom_digital2, custom_digital3, custom_digital4, custom_digital5, custom_digital6, custom_digital7, custom_digital8 )
269 | 1 | MODBUS_OUTPUT_RANGE_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
270 | 1 | MODBUS_OUTPUT_RANGE_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
271 | 1 | MODBUS_OUTPUT_RANGE_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
272 | 1 | MODBUS_OUTPUT_RANGE_4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
273 | 1 | MODBUS_OUTPUT_RANGE_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
274 | 1 | MODBUS_OUTPUT_RANGE_6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
275 | 1 | MODBUS_OUTPUT_RANGE_7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
276 | 1 | MODBUS_OUTPUT_RANGE_8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
277 | 1 | MODBUS_OUTPUT_RANGE_9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
278 | 1 | MODBUS_OUTPUT_RANGE_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
279 | 1 | MODBUS_OUTPUT_RANGE_11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
280 | 1 | MODBUS_OUTPUT_RANGE_12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
281 | 1 | MODBUS_OUTPUT_RANGE_13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
282 | 1 | MODBUS_OUTPUT_SWITCH1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0 - OFF, 1 - HAND, 2 - AUTO
283 | 1 | MODBUS_OUTPUT_SWITCH2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
284 | 1 | MODBUS_OUTPUT_SWITCH3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
285 | 1 | MODBUS_OUTPUT_SWITCH4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
286 | 1 | MODBUS_OUTPUT_SWITCH5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
287 | 1 | MODBUS_OUTPUT_SWITCH6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
288 | 1 | MODBUS_OUTPUT_SWITCH7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
289 | 1 | MODBUS_OUTPUT_SWITCH8 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
290 | 1 | MODBUS_OUTPUT_SWITCH9 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
291 | 1 | MODBUS_OUTPUT_SWITCH10 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
292 | 1 | MODBUS_OUTPUT_SWITCH11 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
293 | 1 | MODBUS_OUTPUT_SWITCH12 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
294 | 1 | MODBUS_OUTPUT_SWITCH13 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
295 | 1 | MODBUS_OUTPUT_SWITCH14 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
342 | 1 | MODBUS_OUTPUT_AD0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 0
343 | 1 | MODBUS_OUTPUT_AD1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 1
344 | 1 | MODBUS_OUTPUT_AD2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 2
345 | 1 | MODBUS_OUTPUT_AD3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 3
346 | 1 | MODBUS_OUTPUT_AD4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 4
347 | 1 | MODBUS_OUTPUT_AD5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 5
348 | 1 | MODBUS_OUTPUT_AD6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 6
349 | 1 | MODBUS_OUTPUT_AD7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 7
350 | 1 | MODBUS_OUTPUT_AD8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 8
351 | 1 | MODBUS_OUTPUT_AD9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 9
352 | 1 | MODBUS_OUTPUT_AD10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 10
353 | 1 | MODBUS_OUTPUT_AD11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 11
354 | 1 | MODBUS_OUTPUT_AD12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 12
355 | 1 | MODBUS_OUTPUT_AD13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 13
800 | 1 | MODBUS_RESET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 1-> reset to factory, other -> reset
9400 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_1 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output1 relinquish
9401 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_1 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output1 relinquish
9402 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_2 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output2 relinquish
9403 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_2 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output2 relinquish
9404 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_3 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output3 relinquish
9405 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_3 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output3 relinquish
9406 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_4 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output4 relinquish
9407 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_4 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output4 relinquish
9408 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_5 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output5 relinquish
9409 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_5 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output5 relinquish
9410 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_6 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output6 relinquish
9411 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_6 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output6 relinquish
9412 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_7 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output7 relinquish
9413 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_7 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output7 relinquish
9414 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_8 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output8 relinquish
9415 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_8 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output8 relinquish
9416 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_9 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output9 relinquish
9417 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_9 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output9 relinquish
9418 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_10 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output10 relinquish
9419 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_10 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output10 relinquish
9420 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_11 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output11 relinquish
9421 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_11 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output11 relinquish
9422 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_12 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output12 relinquish
9423 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_12 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output12 relinquish
9424 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_13 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output13 relinquish
9425 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_13 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output13 relinquish
9426 | 1 | MODBUS_OUTPUT_RELINQUISH_HI_14 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | high word of output14 relinquish
9427 | 1 | MODBUS_OUTPUT_RELINQUISH_LO_14 | 03_06 Read Holding and Write Single | Floating HI_LO/1000 | low word of output14 relinquish

## T322AI
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description | Unit
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
11 | 1 | MODBUS_ISP_VERSION | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | bootloader revision
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | baudrate 0=9600,1=19200,2=38400,3=57600,4=115200,5=76800
21 | 1 | MODBUS_PROTOCOL_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | protocal type. 0=mstp, 3=modbus
22 | 2 | MODBUS_INSTANCE_HIGH | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | high word of instance
23 | 2 | MODBUS_INSTANCE_LOW | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | low word of instance
30 | 1 | MODBUS_OUTPUT_DEAD_MASTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | dead master of outputs
37 | 1 | MODBUS_MAX_MASTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
38 | 1 | MODBUS_BACNET_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
39 | 1 | MODBUS_STATION_NUM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
40 | 6 | MODBUS_MAC | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC address
46 | 1 | MODBUS_IP_MODE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | IP mode. 0=static IP; 1= DHCP
47 | 1 | MODBUS_IP_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
48 | 1 | MODBUS_IP_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
49 | 1 | MODBUS_IP_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
50 | 1 | MODBUS_IP_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP address
51 | 1 | MODBUS_SUBNET_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
52 | 1 | MODBUS_SUBNET_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
53 | 1 | MODBUS_SUBNET_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
54 | 1 | MODBUS_SUBNET_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub mask address
55 | 1 | MODBUS_GETWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
56 | 1 | MODBUS_GETWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
57 | 1 | MODBUS_GETWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
58 | 1 | MODBUS_GETWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | gateway
59 | 1 | MODBUS_TCPSERVER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0,TCP server
60 | 1 | MODBUS_TCP_LISTEN_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | listen port at TCP server mode
61 | 1 | MODBUS_GHOST_IP_MODE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Ghost IP mode. 0=static IP; 1= DHCP
62 | 1 | MODBUS_GHOST_IP_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
63 | 1 | MODBUS_GHOST_IP_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
64 | 1 | MODBUS_GHOST_IP_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
65 | 1 | MODBUS_GHOST_IP_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost IP address
66 | 1 | MODBUS_GHOST_SUBNET_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
67 | 1 | MODBUS_GHOST_SUBNET_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
68 | 1 | MODBUS_GHOST_SUBNET_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
69 | 1 | MODBUS_GHOST_SUBNET_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost sub mask address
70 | 1 | MODBUS_GHOST_GETWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
71 | 1 | MODBUS_GHOST_GETWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
72 | 1 | MODBUS_GHOST_GETWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
73 | 1 | MODBUS_GHOST_GETWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Ghost gateway
74 | 1 | MODBUS_GHOST_TCPSERVER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0,TCP server
75 | 1 | MODBUS_GHOST_TCP_LISTEN_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | listen port at TCP server mode
76 | 1 | MODBUS_WRITE_GHOST_SYSTEM | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
80 | 1 | MODBUS_REPOWER_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | output resume to OFF or last status
90 | 1 | MODBUS_BACNET_VENDOR_ID | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
93 | 1 | MODBUS_MAC_ENABLE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
99 | 1 | MODBUS_SERINALNUMBER_WRITE_FLAG | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
100 | 2 | MODBUS_AI_CHANNLE0_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 0 high byte
101 | 2 | MODBUS_AI_CHANNLE0_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 0 low byte
102 | 2 | MODBUS_AI_CHANNLE1_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 1 high byte
103 | 2 | MODBUS_AI_CHANNLE1_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 1 low byte
104 | 2 | MODBUS_AI_CHANNLE2_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 2 high byte
105 | 2 | MODBUS_AI_CHANNLE2_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 2 low byte
106 | 2 | MODBUS_AI_CHANNLE3_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 3 high byte
107 | 2 | MODBUS_AI_CHANNLE3_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 3 low byte
108 | 2 | MODBUS_AI_CHANNLE4_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 4 high byte
109 | 2 | MODBUS_AI_CHANNLE4_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 4 low byte
110 | 2 | MODBUS_AI_CHANNLE5_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 5 high byte
111 | 2 | MODBUS_AI_CHANNLE5_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 5 low byte
112 | 2 | MODBUS_AI_CHANNLE6_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 6 high byte
113 | 2 | MODBUS_AI_CHANNLE6_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 6 low byte
114 | 2 | MODBUS_AI_CHANNLE7_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 7 high byte
115 | 2 | MODBUS_AI_CHANNLE7_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 7 low byte
116 | 2 | MODBUS_AI_CHANNLE8_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 8 high byte
117 | 2 | MODBUS_AI_CHANNLE8_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 8 low byte
118 | 2 | MODBUS_AI_CHANNLE9_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 9 high byte
119 | 2 | MODBUS_AI_CHANNLE9_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 9 low byte
120 | 2 | MODBUS_AI_CHANNLE10_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 10 high byte
121 | 2 | MODBUS_AI_CHANNLE10_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 10 low byte
122 | 2 | MODBUS_AI_CHANNLE11_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 11 high byte
123 | 2 | MODBUS_AI_CHANNLE11_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 11 low byte
124 | 2 | MODBUS_AI_CHANNLE12_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 12 high byte
125 | 2 | MODBUS_AI_CHANNLE12_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 12 low byte
126 | 2 | MODBUS_AI_CHANNLE13_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 13 high byte
127 | 2 | MODBUS_AI_CHANNLE13_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 13 low byte
128 | 2 | MODBUS_AI_CHANNLE14_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 14 high byte
129 | 2 | MODBUS_AI_CHANNLE14_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 14 low byte
130 | 2 | MODBUS_AI_CHANNLE15_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 15 high byte
131 | 2 | MODBUS_AI_CHANNLE15_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 15 low byte
132 | 2 | MODBUS_AI_CHANNLE16_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 16 high byte
133 | 2 | MODBUS_AI_CHANNLE16_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 16 low byte
134 | 2 | MODBUS_AI_CHANNLE17_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 17 high byte
135 | 2 | MODBUS_AI_CHANNLE17_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 17 low byte
136 | 2 | MODBUS_AI_CHANNLE18_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 18 high byte
137 | 2 | MODBUS_AI_CHANNLE18_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 18 low byte
138 | 2 | MODBUS_AI_CHANNLE19_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 19 high byte
139 | 2 | MODBUS_AI_CHANNLE19_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 19 low byte
140 | 2 | MODBUS_AI_CHANNLE20_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 20 high byte
141 | 2 | MODBUS_AI_CHANNLE20_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 20 low byte
142 | 2 | MODBUS_AI_CHANNLE21_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 21 high byte
143 | 2 | MODBUS_AI_CHANNLE21_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | analog input 21 low byte
200 | 1 | MODBUS_AI_FILTER0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 0 filter
201 | 1 | MODBUS_AI_FILTER1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 1 filter
202 | 1 | MODBUS_AI_FILTER2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 2 filter
203 | 1 | MODBUS_AI_FILTER3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 3 filter
204 | 1 | MODBUS_AI_FILTER4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 4 filter
205 | 1 | MODBUS_AI_FILTER5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 5 filter
206 | 1 | MODBUS_AI_FILTER6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 6 filter
207 | 1 | MODBUS_AI_FILTER7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 7 filter
208 | 1 | MODBUS_AI_FILTER8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 8 filter
209 | 1 | MODBUS_AI_FILTER9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 9 filter
210 | 2 | MODBUS_AI_FILTER10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 10 filter
211 | 2 | MODBUS_AI_FILTER11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 11 filter
212 | 2 | MODBUS_AI_FILTER12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 12 filter
213 | 2 | MODBUS_AI_FILTER13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 13 filter
214 | 2 | MODBUS_AI_FILTER14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 14 filter
215 | 2 | MODBUS_AI_FILTER15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 15 filter
216 | 2 | MODBUS_AI_FILTER16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 16 filter
217 | 2 | MODBUS_AI_FILTER17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 17 filter
218 | 1 | MODBUS_AI_FILTER18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 18 filter
219 | 1 | MODBUS_AI_FILTER19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 19 filter
220 | 1 | MODBUS_AI_FILTER20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 20 filter
221 | 1 | MODBUS_AI_FILTER21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 21 filter
225 | 1 | MODBUS_AI_RANGE0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 0 range. if analog inputs (not_used_input = 0, Y3K_40_150DegC, Y3K_40_300DegF, R10K_40_120DegC, R10K_40_250DegF, R3K_40_150DegC, R3K_40_300DegF, KM10K_40_120DegC, KM10K_40_250DegF, A10K_50_110DegC, A10K_60_200DegF, V0_5, I0_100Amps, I0_20ma, I0_20psi, N0_2_32counts, N0_3000FPM_0_5V, P0_100_0_5V, P0_100_4_20ma, P0_255p_min, table1, table2, table3, table4, table5,100 - HI_SPEED_COUNTER ), if digital inputs(not_used_input = 0,OFF_ON, CLOSED_OPEN, STOP_START, DISABLED_ENABLED, NORMAL_ALARM, NORMAL_HIGH, NORMAL_LOW, NO_YES, COOL_HEAT, UNOCCUPIED_OCCUPIED, LOW_HIGH, ON_OFF , OPEN_CLOSED, START_STOP, ENABLED_DISABLED, ALARM_NORMAL, HIGH_NORMAL, LOW_NORMAL, YES_NO, HEAT_COOL, OCCUPIED_UNOCCUPIED, HIGH_LOW, custom_digital1, custom_digital2, custom_digital3, custom_digital4, custom_digital5, custom_digital6, custom_digital7, custom_digital8 )
226 | 1 | MODBUS_AI_RANGE1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 1 range
227 | 1 | MODBUS_AI_RANGE2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 2 range
228 | 1 | MODBUS_AI_RANGE3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 3 range
229 | 1 | MODBUS_AI_RANGE4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 4 range
230 | 1 | MODBUS_AI_RANGE5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 5 range
231 | 1 | MODBUS_AI_RANGE6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 6 range
232 | 1 | MODBUS_AI_RANGE7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 7 range
233 | 1 | MODBUS_AI_RANGE8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 8 range
234 | 1 | MODBUS_AI_RANGE9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 9 range
235 | 1 | MODBUS_AI_RANGE10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 10 range
236 | 1 | MODBUS_AI_RANGE11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 11 range
237 | 1 | MODBUS_AI_RANGE12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 12 range
238 | 1 | MODBUS_AI_RANGE13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 13 range
239 | 1 | MODBUS_AI_RANGE14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 14 range
240 | 1 | MODBUS_AI_RANGE15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 15 range
241 | 1 | MODBUS_AI_RANGE16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 16 range
242 | 1 | MODBUS_AI_RANGE17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 17 range
243 | 1 | MODBUS_AI_RANGE18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 18 range
244 | 1 | MODBUS_AI_RANGE19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 19 range
245 | 1 | MODBUS_AI_RANGE20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 20 range
246 | 1 | MODBUS_AI_RANGE21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | analog input 21 range
247 | 1 | MODBUS_AUTO_MANUAL_0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 0
248 | 1 | MODBUS_AUTO_MANUAL_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 1
249 | 1 | MODBUS_AUTO_MANUAL_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 2
250 | 1 | MODBUS_AUTO_MANUAL_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 3
251 | 1 | MODBUS_AUTO_MANUAL_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 4
252 | 1 | MODBUS_AUTO_MANUAL_5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 5
253 | 1 | MODBUS_AUTO_MANUAL_6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 6
254 | 1 | MODBUS_AUTO_MANUAL_7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 7
255 | 1 | MODBUS_AUTO_MANUAL_8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 8
256 | 1 | MODBUS_AUTO_MANUAL_9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 9
257 | 1 | MODBUS_AUTO_MANUAL_10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 10
258 | 1 | MODBUS_AUTO_MANUAL_11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 11
259 | 1 | MODBUS_AUTO_MANUAL_12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 12
260 | 1 | MODBUS_AUTO_MANUAL_13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 13
261 | 1 | MODBUS_AUTO_MANUAL_14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 14
262 | 1 | MODBUS_AUTO_MANUAL_15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 15
263 | 1 | MODBUS_AUTO_MANUAL_16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 16
264 | 1 | MODBUS_AUTO_MANUAL_17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 17
265 | 1 | MODBUS_AUTO_MANUAL_18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 18
266 | 1 | MODBUS_AUTO_MANUAL_19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 19
267 | 1 | MODBUS_AUTO_MANUAL_20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 20
268 | 1 | MODBUS_AUTO_MANUAL_21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | auto manual setting for input 21
269 | 1 | MODBUS_AI_DI_AI0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input0 ( 0 - digital 1 - analog)
270 | 1 | MODBUS_AI_DI_AI1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input1
271 | 1 | MODBUS_AI_DI_AI2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input2
272 | 1 | MODBUS_AI_DI_AI3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input3
273 | 1 | MODBUS_AI_DI_AI4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input4
274 | 1 | MODBUS_AI_DI_AI5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input5
275 | 1 | MODBUS_AI_DI_AI6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input6
276 | 1 | MODBUS_AI_DI_AI7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input7
277 | 1 | MODBUS_AI_DI_AI8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input8
278 | 1 | MODBUS_AI_DI_AI9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input9
279 | 1 | MODBUS_AI_DI_AI10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input10
280 | 1 | MODBUS_AI_DI_AI11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input11
281 | 1 | MODBUS_AI_DI_AI12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input12
282 | 1 | MODBUS_AI_DI_AI13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input13
283 | 1 | MODBUS_AI_DI_AI14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input14
284 | 1 | MODBUS_AI_DI_AI15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input15
285 | 1 | MODBUS_AI_DI_AI16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input16
286 | 1 | MODBUS_AI_DI_AI17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input17
287 | 1 | MODBUS_AI_DI_AI18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input18
288 | 1 | MODBUS_AI_DI_AI19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input19
289 | 1 | MODBUS_AI_DI_AI20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input20
290 | 1 | MODBUS_AI_DI_AI21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting for input21
291 | 1 | MODBUS_AI_JUPER0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
292 | 1 | MODBUS_AI_JUPER1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
293 | 1 | MODBUS_AI_JUPER2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
294 | 1 | MODBUS_AI_JUPER3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
295 | 1 | MODBUS_AI_JUPER4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
296 | 1 | MODBUS_AI_JUPER5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
297 | 1 | MODBUS_AI_JUPER6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
298 | 1 | MODBUS_AI_JUPER7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
299 | 1 | MODBUS_AI_JUPER8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
300 | 1 | MODBUS_AI_JUPER9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
301 | 1 | MODBUS_AI_JUPER10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
302 | 1 | MODBUS_AI_JUPER11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
303 | 1 | MODBUS_AI_JUPER12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
304 | 1 | MODBUS_AI_JUPER13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
305 | 1 | MODBUS_AI_JUPER14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
306 | 1 | MODBUS_AI_JUPER15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
307 | 1 | MODBUS_AI_JUPER16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
308 | 1 | MODBUS_AI_JUPER17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
309 | 1 | MODBUS_AI_JUPER18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
310 | 1 | MODBUS_AI_JUPER19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
311 | 1 | MODBUS_AI_JUPER20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
312 | 1 | MODBUS_AI_JUPER21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
313 | 1 | MODBUS_CAL_SIGN0 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 0
314 | 1 | MODBUS_CAL_SIGN1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 1
315 | 1 | MODBUS_CAL_SIGN2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 2
316 | 1 | MODBUS_CAL_SIGN3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 3
317 | 1 | MODBUS_CAL_SIGN4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 4
318 | 1 | MODBUS_CAL_SIGN5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 5
319 | 1 | MODBUS_CAL_SIGN6 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 6
320 | 1 | MODBUS_CAL_SIGN7 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 7
321 | 1 | MODBUS_CAL_SIGN8 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 8
322 | 1 | MODBUS_CAL_SIGN9 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 9
323 | 1 | MODBUS_CAL_SIGN10 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 10
324 | 1 | MODBUS_CAL_SIGN11 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 11
325 | 1 | MODBUS_CAL_SIGN12 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 12
326 | 1 | MODBUS_CAL_SIGN13 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 13
327 | 1 | MODBUS_CAL_SIGN14 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 14
328 | 1 | MODBUS_CAL_SIGN15 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 15
329 | 1 | MODBUS_CAL_SIGN16 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 16
330 | 1 | MODBUS_CAL_SIGN17 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 17
331 | 1 | MODBUS_CAL_SIGN18 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 18
332 | 1 | MODBUS_CAL_SIGN19 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 19
333 | 1 | MODBUS_CAL_SIGN20 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 20
334 | 1 | MODBUS_CAL_SIGN21 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Analog input calibration sign 21
335 | 2 | MODBUS_CAL0_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input0
336 | 2 | MODBUS_CAL0_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input0
337 | 2 | MODBUS_CAL1_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input1
338 | 2 | MODBUS_CAL1_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input1
339 | 2 | MODBUS_CAL2_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input2
340 | 2 | MODBUS_CAL2_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input2
341 | 2 | MODBUS_CAL3_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input3
342 | 2 | MODBUS_CAL3_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input3
343 | 2 | MODBUS_CAL4_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input4
344 | 2 | MODBUS_CAL4_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input4
345 | 2 | MODBUS_CAL5_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input5
346 | 2 | MODBUS_CAL5_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input5
347 | 2 | MODBUS_CAL6_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input6
348 | 2 | MODBUS_CAL6_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input6
349 | 2 | MODBUS_CAL7_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input7
350 | 2 | MODBUS_CAL7_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input7
351 | 2 | MODBUS_CAL8_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input8
352 | 2 | MODBUS_CAL8_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input8
353 | 2 | MODBUS_CAL9_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input9
354 | 2 | MODBUS_CAL9_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input9
355 | 2 | MODBUS_CAL10_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input10
356 | 2 | MODBUS_CAL10_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input10
357 | 2 | MODBUS_CAL11_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input11
358 | 2 | MODBUS_CAL11_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input11
359 | 2 | MODBUS_CAL12_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input12
360 | 2 | MODBUS_CAL12_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input12
361 | 2 | MODBUS_CAL13_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input13
362 | 2 | MODBUS_CAL13_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input13
363 | 2 | MODBUS_CAL14_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input14
364 | 2 | MODBUS_CAL14_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input14
365 | 2 | MODBUS_CAL15_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input15
366 | 2 | MODBUS_CAL15_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input15
367 | 2 | MODBUS_CAL16_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input16
368 | 2 | MODBUS_CAL16_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input16
369 | 2 | MODBUS_CAL17_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input17
370 | 2 | MODBUS_CAL17_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input17
371 | 2 | MODBUS_CAL18_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input18
372 | 2 | MODBUS_CAL18_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input18
373 | 2 | MODBUS_CAL19_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input19
374 | 2 | MODBUS_CAL19_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input19
375 | 2 | MODBUS_CAL20_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input20
376 | 2 | MODBUS_CAL20_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input20
377 | 2 | MODBUS_CAL21_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value high byte input21
378 | 2 | MODBUS_CAL21_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | calibrate value low byte input21
379 | 1 | MODBUS_AI0_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
380 | 1 | MODBUS_AI1_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
381 | 1 | MODBUS_AI2_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
382 | 1 | MODBUS_AI3_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
383 | 1 | MODBUS_AI4_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
384 | 1 | MODBUS_AI5_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
385 | 1 | MODBUS_AI6_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
386 | 1 | MODBUS_AI7_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
387 | 1 | MODBUS_AI8_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
388 | 1 | MODBUS_AI9_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
389 | 1 | MODBUS_AI10_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
390 | 1 | MODBUS_AI11_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
391 | 1 | MODBUS_AI12_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
392 | 1 | MODBUS_AI13_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
393 | 1 | MODBUS_AI14_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
394 | 1 | MODBUS_AI15_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
395 | 1 | MODBUS_AI16_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
396 | 1 | MODBUS_AI17_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
397 | 1 | MODBUS_AI18_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
398 | 1 | MODBUS_AI19_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
399 | 1 | MODBUS_AI20_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
400 | 1 | MODBUS_AI21_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
401 | 1 | MODBUS_AI22_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
800 | 1 | MODBUS_RESET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 1-> reset to factory, other -> reset

## T3PT12
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
100 | 2 | MODBUS_TEMP0 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 0
101 | 2 | MODBUS_TEMP1 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 1
102 | 2 | MODBUS_TEMP2 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 2
103 | 2 | MODBUS_TEMP3 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 3
104 | 2 | MODBUS_TEMP4 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 4
105 | 2 | MODBUS_TEMP5 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 5
106 | 2 | MODBUS_TEMP6 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 6
107 | 2 | MODBUS_TEMP7 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 7
108 | 2 | MODBUS_TEMP8 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 8
109 | 2 | MODBUS_TEMP9 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 9
110 | 2 | MODBUS_TEMP10 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 10
111 | 2 | MODBUS_TEMP11 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer | Temperature of channel 11
112 | 1 | MODBUS_SENSOR0_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 0
113 | 1 | MODBUS_SENSOR1_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 1
114 | 1 | MODBUS_SENSOR2_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 2
115 | 1 | MODBUS_SENSOR3_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 3
116 | 1 | MODBUS_SENSOR4_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 4
117 | 1 | MODBUS_SENSOR5_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 5
118 | 1 | MODBUS_SENSOR6_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 6
119 | 1 | MODBUS_SENSOR7_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 7
120 | 1 | MODBUS_SENSOR8_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 8
121 | 1 | MODBUS_SENSOR9_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 9
122 | 1 | MODBUS_SENSOR10_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 10
123 | 1 | MODBUS_SENSOR11_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor type selection of channel 11
148 | 1 | MODBUS_CHANNEL0_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 0
149 | 1 | MODBUS_CHANNEL1_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 1
150 | 1 | MODBUS_CHANNEL2_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 2
151 | 1 | MODBUS_CHANNEL3_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 3
152 | 1 | MODBUS_CHANNEL4_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 4
153 | 1 | MODBUS_CHANNEL5_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 5
154 | 1 | MODBUS_CHANNEL6_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 6
155 | 1 | MODBUS_CHANNEL7_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 7
156 | 1 | MODBUS_CHANNEL8_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 8
157 | 1 | MODBUS_CHANNEL9_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 9
158 | 1 | MODBUS_CHANNEL10_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 10
159 | 1 | MODBUS_CHANNEL11_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Range of channel 11
162 | 1 | MODBUS_CAL_FLAG | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
163 | 1 | MODBUS_CHANNEL0_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 0
164 | 1 | MODBUS_CHANNEL1_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 1
165 | 1 | MODBUS_CHANNEL2_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 2
166 | 1 | MODBUS_CHANNEL3_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 3
167 | 1 | MODBUS_CHANNEL4_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 4
168 | 1 | MODBUS_CHANNEL5_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 5
169 | 1 | MODBUS_CHANNEL6_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 6
170 | 1 | MODBUS_CHANNEL7_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 7
171 | 1 | MODBUS_CHANNEL8_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 8
172 | 1 | MODBUS_CHANNEL9_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 9
173 | 1 | MODBUS_CHANNEL10_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 10
174 | 1 | MODBUS_CHANNEL11_A_D | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | digit and analog setting of channel 11
200 | 1 | MODBUS_CHANNEL0_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 0 filter
201 | 1 | MODBUS_CHANNEL1_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 1 filter
202 | 1 | MODBUS_CHANNEL2_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 2 filter
203 | 1 | MODBUS_CHANNEL3_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 3 filter
204 | 1 | MODBUS_CHANNEL4_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 4 filter
205 | 1 | MODBUS_CHANNEL5_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 5 filter
206 | 1 | MODBUS_CHANNEL6_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 6 filter
207 | 1 | MODBUS_CHANNEL7_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 7 filter
208 | 1 | MODBUS_CHANNEL8_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 8 filter
209 | 1 | MODBUS_CHANNEL9_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 9 filter
210 | 1 | MODBUS_CHANNEL10_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 10 filter
211 | 1 | MODBUS_CHANNEL11_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel 11 filter
220 | 2 | MODBUS_POINT_AD0_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 0 high byte
221 | 2 | MODBUS_POINT_AD0_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 0 low byte
222 | 2 | MODBUS_POINT_AD1_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 1 high byte
223 | 2 | MODBUS_POINT_AD1_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 1 low byte
224 | 2 | MODBUS_POINT_AD2_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 2 high byte
225 | 2 | MODBUS_POINT_AD2_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 2 low byte
226 | 2 | MODBUS_POINT_AD3_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 3 high byte
227 | 2 | MODBUS_POINT_AD3_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 3 low byte
228 | 2 | MODBUS_POINT_AD4_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 4 high byte
229 | 2 | MODBUS_POINT_AD4_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 4 low byte
230 | 2 | MODBUS_POINT_AD5_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 5 high byte
231 | 2 | MODBUS_POINT_AD5_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 5 low byte
232 | 2 | MODBUS_POINT_AD6_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 6 high byte
233 | 2 | MODBUS_POINT_AD6_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 6 low byte
234 | 2 | MODBUS_POINT_AD7_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 7 high byte
235 | 2 | MODBUS_POINT_AD7_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | raw AD for calibration resister 7 low byte
236 | 2 | MODBUS_CHANNEL_AD0_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 0 AD value high byte
237 | 2 | MODBUS_CHANNEL_AD0_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 0 AD value low byte
238 | 2 | MODBUS_CHANNEL_AD1_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 1 AD value high byte
239 | 2 | MODBUS_CHANNEL_AD1_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 1 AD value low byte
240 | 2 | MODBUS_CHANNEL_AD2_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 2 AD value high byte
241 | 2 | MODBUS_CHANNEL_AD2_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 2 AD value low byte
242 | 2 | MODBUS_CHANNEL_AD3_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 3 AD value high byte
243 | 2 | MODBUS_CHANNEL_AD3_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 3 AD value low byte
244 | 2 | MODBUS_CHANNEL_AD4_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 4 AD value high byte
245 | 2 | MODBUS_CHANNEL_AD4_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 4 AD value low byte
246 | 2 | MODBUS_CHANNEL_AD5_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 5 AD value high byte
247 | 2 | MODBUS_CHANNEL_AD5_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 5 AD value low byte
248 | 2 | MODBUS_CHANNEL_AD6_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 6 AD value high byte
249 | 2 | MODBUS_CHANNEL_AD6_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 6 AD value low byte
250 | 2 | MODBUS_CHANNEL_AD7_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 7 AD value high byte
251 | 2 | MODBUS_CHANNEL_AD7_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 7 AD value low byte
252 | 2 | MODBUS_CHANNEL_AD8_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 8 AD value high byte
253 | 2 | MODBUS_CHANNEL_AD8_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 8 AD value low byte
254 | 2 | MODBUS_CHANNEL_AD9_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 9 AD value high byte
255 | 2 | MODBUS_CHANNEL_AD9_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 9 AD value low byte
256 | 2 | MODBUS_CHANNEL_AD10_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 10 AD value high byte
257 | 2 | MODBUS_CHANNEL_AD10_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 10 AD value low byte
258 | 2 | MODBUS_CHANNEL_AD11_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 11 AD value high byte
259 | 2 | MODBUS_CHANNEL_AD11_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Channel 11 AD value low byte
800 | 1 | MODBUS_RESET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 1-> reset to factory, other -> reset

## BTU Meter
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
14 | 1 | MODBUS_LOCK | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
16 | 1 | MODBUS_UPDATE_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
104 | 1 | MODBUS_TOTAL_HEAT_HIGH | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
105 | 1 | MODBUS_TOTAL_HEAT_LOW | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
106 | 2 | MODBUS_UP_PT_1000_SENSOR_TEMPERATURE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
107 | 2 | MODBUS_DOWN_PT_1000_SENSOR_TEMPERATURE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
109 | 2 | MODBUS_UP_PT_1000_SENSOR_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
110 | 2 | MODBUS_DOWN_PT_1000_SENSOR_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
111 | 2 | MODBUS_TEMPERATURE_UNIT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
302 | 2 | MODBUS_CURRENT_FLOW_RATE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
304 | 2 | MODBUS_POSITIVE_DIRECTION_TOTAL_FLOW_INTEGER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
306 | 2 | MODBUS_POSITIVE_DIRECTION_TOTAL_FLOW_FLOAT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
308 | 2 | MODBUS_NEGATIVE_DIRECTION_TOTAL_FLOW_INTEGER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
310 | 2 | MODBUS_NEGATIVE_DIRECTION_TOTAL_FLOW_FLOAT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
312 | 1 | MODBUS_FLOW_UNIT | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
313 | 1 | MODBUS_TOTAL_FLOW_UNIT | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
314 | 1 | MODBUS_PIPE_EMPTY_WARNING | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer

## Power Meter
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0:9600 1:19200 2:38400 3:57600 4:115200 5:76800
40 | 1 | MODBUS_MAC_ADDRESS_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
41 | 1 | MODBUS_MAC_ADDRESS_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
42 | 1 | MODBUS_MAC_ADDRESS_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
43 | 1 | MODBUS_MAC_ADDRESS_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
44 | 1 | MODBUS_MAC_ADDRESS_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
45 | 1 | MODBUS_MAC_ADDRESS_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
46 | 1 | MODBUS_IP_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
47 | 1 | MODBUS_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
48 | 1 | MODBUS_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
49 | 1 | MODBUS_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
50 | 1 | MODBUS_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
51 | 1 | MODBUS_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
52 | 1 | MODBUS_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
53 | 1 | MODBUS_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
54 | 1 | MODBUS_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
55 | 1 | MODBUS_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
56 | 1 | MODBUS_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
57 | 1 | MODBUS_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
58 | 1 | MODBUS_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
61 | 1 | MODBUS_GHOST_IP_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
62 | 1 | MODBUS_GHOST_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
63 | 1 | MODBUS_GHOST_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
64 | 1 | MODBUS_GHOST_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
65 | 1 | MODBUS_GHOST_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
66 | 1 | MODBUS_GHOST_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
67 | 1 | MODBUS_GHOST_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
68 | 1 | MODBUS_GHOST_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
69 | 1 | MODBUS_GHOST_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
70 | 1 | MODBUS_GHOST_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
71 | 1 | MODBUS_GHOST_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
72 | 1 | MODBUS_GHOST_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
73 | 1 | MODBUS_GHOST_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
103 | 1 | MODBUS_PM0_VOLTAGE_FREQUENCY | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
104 | 1 | MODBUS_PM0_PERIOD | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
117 | 1 | MODBUS_PM0_VRMS_VALUE | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
118 | 1 | MODBUS_PM0_IRMS_VALUE | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
120 | 1 | MODBUS_PM0_VRMS_CAL_VALUE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
125 | 1 | MODBUS_PM0_IRMS_CAL_VALUE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
130 | 2 | MODBUS_PM0_ACTIVE_POWER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
148 | 1 | MODBUS_PM0_LAENERGY_HIGH | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
149 | 1 | MODBUS_PM0_LAENERGY_LOW | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
160 | 1 | MODBUS_PM0_FACTOR | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
203 | 1 | MODBUS_PM1_VOLTAGE_FREQUENCY | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
204 | 1 | MODBUS_PM1_PERIOD | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
217 | 1 | MODBUS_PM1_VRMS_VALUE | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
218 | 1 | MODBUS_PM1_IRMS_VALUE | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
220 | 1 | MODBUS_PM1_VRMS_CAL_VALUE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
225 | 1 | MODBUS_PM1_IRMS_CAL_VALUE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
230 | 2 | MODBUS_PM1_ACTIVE_POWER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
248 | 1 | MODBUS_PM1_LAENERGY_HIGH | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
249 | 1 | MODBUS_PM1_LAENERGY_LOW | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
260 | 1 | MODBUS_PM1_FACTOR | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
303 | 1 | MODBUS_PM2_VOLTAGE_FREQUENCY | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
304 | 1 | MODBUS_PM2_PERIOD | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
317 | 1 | MODBUS_PM2_VRMS_VALUE | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
318 | 1 | MODBUS_PM2_IRMS_VALUE | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
320 | 1 | MODBUS_PM2_VRMS_CAL_VALUE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
325 | 1 | MODBUS_PM2_IRMS_CAL_VALUE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
330 | 2 | MODBUS_PM2_ACTIVE_POWER | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
348 | 1 | MODBUS_PM2_LAENERGY_HIGH | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
349 | 1 | MODBUS_PM2_LAENERGY_LOW | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
360 | 1 | MODBUS_PM2_FACTOR | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
1045 | 1 | MODBUS_INPUT_VALUE_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
1046 | 1 | MODBUS_INPUT_VALUE_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
1047 | 1 | MODBUS_INPUT_VALUE_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
1048 | 1 | MODBUS_INPUT_VALUE_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
1050 | 1 | MODBUS_OUTPUT_VALUE_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
1051 | 1 | MODBUS_OUTPUT_VALUE_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
1052 | 1 | MODBUS_OUTPUT_VALUE_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
1053 | 1 | MODBUS_OUTPUT_VALUE_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
1070 | 1 | MODBUS_SELECT_CT_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
1071 | 2 | MODBUS_CT_RATIO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
1080 | 2 | MODBUS_TOTAL_ACTIVE_POWER | 03 Read Holding Registers (4x) | 32 Bit Signed Integer LO_HI
1082 | 2 | MODBUS_TOTAL_ENERGY | 03 Read Holding Registers (4x) | 32 Bit Signed Integer HI_LO

## T36CTA
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
100 | 2 | MODBUS_DO_CHANNLE0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
101 | 2 | MODBUS_DO_CHANNLE1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
102 | 2 | MODBUS_SWITCH_BANK0 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
103 | 2 | MODBUS_SWITCH_BANK1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
104 | 2 | MODBUS_AI_CHANNLE0_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
105 | 2 | MODBUS_AI_CHANNLE0_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
106 | 2 | MODBUS_AI_CHANNLE1_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
107 | 2 | MODBUS_AI_CHANNLE1_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
108 | 2 | MODBUS_AI_CHANNLE2_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
109 | 2 | MODBUS_AI_CHANNLE2_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
110 | 2 | MODBUS_AI_CHANNLE3_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
111 | 2 | MODBUS_AI_CHANNLE3_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
112 | 2 | MODBUS_AI_CHANNLE4_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
113 | 2 | MODBUS_AI_CHANNLE4_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
114 | 2 | MODBUS_AI_CHANNLE5_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
115 | 2 | MODBUS_AI_CHANNLE5_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
116 | 2 | MODBUS_AI_CHANNLE6_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
117 | 2 | MODBUS_AI_CHANNLE6_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
118 | 2 | MODBUS_AI_CHANNLE7_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
119 | 2 | MODBUS_AI_CHANNLE7_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
120 | 2 | MODBUS_AI_CHANNLE8_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
121 | 2 | MODBUS_AI_CHANNLE8_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
122 | 2 | MODBUS_AI_CHANNLE9_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
123 | 2 | MODBUS_AI_CHANNLE9_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
124 | 2 | MODBUS_AI_CHANNLE10_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
125 | 2 | MODBUS_AI_CHANNLE10_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
126 | 2 | MODBUS_AI_CHANNLE11_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
127 | 2 | MODBUS_AI_CHANNLE11_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
128 | 2 | MODBUS_AI_CHANNLE12_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
129 | 2 | MODBUS_AI_CHANNLE12_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
130 | 2 | MODBUS_AI_CHANNLE13_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
131 | 2 | MODBUS_AI_CHANNLE13_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
132 | 2 | MODBUS_AI_CHANNLE14_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
133 | 2 | MODBUS_AI_CHANNLE14_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
134 | 2 | MODBUS_AI_CHANNLE15_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
135 | 2 | MODBUS_AI_CHANNLE15_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
136 | 2 | MODBUS_AI_CHANNLE16_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
137 | 2 | MODBUS_AI_CHANNLE16_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
138 | 2 | MODBUS_AI_CHANNLE17_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
139 | 2 | MODBUS_AI_CHANNLE17_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
140 | 2 | MODBUS_AI_CHANNLE18_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
141 | 2 | MODBUS_AI_CHANNLE18_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
142 | 2 | MODBUS_AI_CHANNLE19_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
143 | 2 | MODBUS_AI_CHANNLE19_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
599 | 1 | MODBUS_RFM69_EXIST | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
600 | 8 | MODBUS_RFM69_ENCRYPT_KEY1 | 16 Write Multiple Registers | Character String HI_LO
608 | 1 | MODBUS_RFM69_NETWORK_ID | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
609 | 1 | MODBUS_RFM69_NODE_ID | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
610 | 4 | MODBUS_RFM69_FREQUENCE | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer HI_LO
612 | 1 | MODBUS_RFM69_ENABLE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
613 | 1 | MODBUS_RFM69_DEADMASTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
614 | 2 | MODBUS_RFM69_BITRATE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
615 | 2 | MODBUS_RFM69_RSSI | 03 Read Holding Registers (4x) | 8 Bit Signed Integer
616 | 1 | MODBUS_RFM69_DEADMASTER_ENABLE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
617 | 2 | MODBUS_POWER_VOLTAGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
669 | 2 | MODBUS_AIR_FLOW_ADC | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
670 | 1 | MODBUS_ACCELERO_ID | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
679 | 2 | MODBUS_ACCELERO_X | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
680 | 2 | MODBUS_ACCELERO_Y | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
681 | 2 | MODBUS_ACCELERO_Z | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
682 | 2 | MODBUS_ACC_SENSITIVITY_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
683 | 2 | MODBUS_ACC_SENSITIVITY_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
684 | 1 | MODBUS_COM_SWITCH | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
685 | 1 | MODBUS_COM_SLAVE_ID | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
686 | 2 | MODBUS_GYROSCOPE_X | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
687 | 2 | MODBUS_GYROSCOPE_Y | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
688 | 2 | MODBUS_GYROSCOPE_Z | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
689 | 1 | MODBUS_CTRL1_XL | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
690 | 1 | MODBUS_CTRL2_G | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
691 | 1 | MODBUS_CTRL3_C | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
692 | 1 | MODBUS_CTRL4_C | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
693 | 1 | MODBUS_CTRL5_C | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
694 | 1 | MODBUS_CTRL6_C | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
695 | 1 | MODBUS_CTRL7_G | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
696 | 1 | MODBUS_CTRL8_XL | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
697 | 1 | MODBUS_CTRL9_XL | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
698 | 1 | MODBUS_CTRL10_C | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer

## ZIGBEE_REPEATER
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
21 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | network controller baudrate 0=9600 1=19200 2-38400 3-57600 4-115200
22 | 2 | MODBUS_PANID | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PANID for zigbee devices
23 | 1 | MODBUS_TYPE_ZIGBEE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Device type of zigbee. 0 means coordinator , 1 means router
24 |  | MODBUS_CHANNEL | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Channel of Zigbee, default channel is channel 13, range 11-26

## PM2_5
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description | Unit
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=9600,1=19200,2=38400,3=57600,4=115200,5=76800
16 | 1 | MODBUS_UPDATE_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
21 | 1 | MODBUS_PROTOCOL_SWITCH | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 3 = MODBUS,0=MSTP.
40 | 1 | MODBUS_MAC_ADDRESS_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
41 | 1 | MODBUS_MAC_ADDRESS_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
42 | 1 | MODBUS_MAC_ADDRESS_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
43 | 1 | MODBUS_MAC_ADDRESS_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
44 | 1 | MODBUS_MAC_ADDRESS_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
45 | 1 | MODBUS_MAC_ADDRESS_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
46 | 1 | MODBUS_IP_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=static IP; 1= DHCP
47 | 1 | MODBUS_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
48 | 1 | MODBUS_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
49 | 1 | MODBUS_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
50 | 1 | MODBUS_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
51 | 1 | MODBUS_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
52 | 1 | MODBUS_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
53 | 1 | MODBUS_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
54 | 1 | MODBUS_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
55 | 1 | MODBUS_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
56 | 1 | MODBUS_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
57 | 1 | MODBUS_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
58 | 1 | MODBUS_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
61 | 1 | MODBUS_GHOST_IP_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_MODE
62 | 1 | MODBUS_GHOST_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
63 | 1 | MODBUS_GHOST_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
64 | 1 | MODBUS_GHOST_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
65 | 1 | MODBUS_GHOST_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
66 | 1 | MODBUS_GHOST_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
67 | 1 | MODBUS_GHOST_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
68 | 1 | MODBUS_GHOST_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
69 | 1 | MODBUS_GHOST_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
70 | 1 | MODBUS_GHOST_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
71 | 1 | MODBUS_GHOST_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
72 | 1 | MODBUS_GHOST_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
73 | 1 | MODBUS_GHOST_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
102 | 2 | MODBUS_AQI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Air Quality Index
103 | 1 | MODBUS_AQI_LEVEL | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | AQI LEVEL. 0 = Good,1=Moderate,2=pool for some, 3=unhealthy,4=more unhealthy,5=hazardous.
104 | 1 | MODBUS_WORK_PERIOD | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the work period. 0 = work all the time. 1~30 minutes.
105 | 2 | MODBUS_PM25_SENSOR_ID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
107 | 1 | MODBUS_PM25_SENSOR_STATUS | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer
109 | 1 | MODBUS_MAIN_DISPLAY_SET | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the pm2.5 sensor status. 0 = offline,1=online
110 | 1 | MODBUS_SCROLL_DISPLAY_SET | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the main display set . bit0:PM25,bit1:pm10,bit2:AQI, each bit indicate if the item will show on the top display. 0: disable 1:enable. Defualt: 0000 0111(Binary), show all 3 items
111 | 1 | MODBUS_MAIN_DISPLAY_SWITCH_TIME | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the scroll display set. bit0:sensor status, bit1:rx/tx,bit2:baudrate,bit3:aqi level. each bit indicate if the item will show on the bottom scroll display. 0: disable 1:enable. Defualt: 0000 0111(Binary), show all 3 items
116 | 1 | MODBUS_PM_OUTPUT_AUTO_MANUAL | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0:Auto 3:Manual
117 | 1 | MODBUS_PM_OUTPUT_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | This value is determined by the jumper position on the board , 1=0-10v, 2=0-5V, 3=4-20mA
118 | 2 | MODBUS_PM10_OUTPUT_MIN_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Default :0
119 | 2 | MODBUS_PM10_OUTPUT_MAX_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Default :1000 PM10 Output range : 0--1000 = 0-100μg/m3 , 0-10000 = 0-1000μg/m3
120 | 2 | MODBUS_PM25_OUTPUT_MIN_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Default :0
121 | 2 | MODBUS_PM25_OUTPUT_MAX_RANGE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Default :1000 PM2.5 Output range : 0--1000 = 0-100μg/m3 , 0-10000 =0-1000 μg/m3
126 | 2 | MODBUS_PM25_WEIGHT_1_0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0.3 to 1.0 μm Mass concentration Unit : μg/m3
127 | 2 | MODBUS_PM25_WEIGHT_2_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0.3 to 2.5 μm
128 | 2 | MODBUS_PM25_WEIGHT_4_0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0.3 to 4 μm
129 | 2 | MODBUS_PM25_WEIGHT_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0.3 to 10μm
130 | 2 | MODBUS_PM25_NUMBER_0_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0.3 to 0.5 Number concentration Unit:1/cm3
131 | 2 | MODBUS_PM25_NUMBER_1_0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0.3 to 1.0
132 | 2 | MODBUS_PM25_NUMBER_2_5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0.3 to 2.5
133 | 2 | MODBUS_PM25_NUMBER_4_0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0.3 to 4.0
134 | 2 | MODBUS_PM25_NUMBER_10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0.3 to 10.0
135 | 1 | MODBUS_PM25_OUTPUT_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | PM2.5 output range ,0 = 0-100ug/m3, 1 = 0-1000ug/m3
136 | 1 | MODBUS_PM25_AREA | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer
137 | 2 | MODBUS_AQI_FIRST_LINE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
138 | 2 | MODBUS_AQI_SECOND_LINE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
139 | 2 | MODBUS_AQI_THIRD_LINE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
140 | 2 | MODBUS_AQI_FOURTH_LINE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
141 | 2 | MODBUS_AQI_FIFTH_LINE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
142 | 1 | MODBUS_PM10_RAND_OFFSET | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | PM10 rand offset value : 0--255
143 | 1 | MODBUS_PM10_OFFSET_ENABLE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0:Disable 1: Enable
3079 | 1 | MODBUS_UART1_PARITY | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0 : None Parity 1: Odd Parity 2:Even Parity

## CO2
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 1 | MODBUS_FIRMWARE_VERSION_LOW | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version low
5 | 1 | MODBUS_FIRMWARE_VERSION_HIGH | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version high
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=9600,1=19200,2=38400,3=57600,4=115200,5=76800
21 | 1 | MODBUS_PROTOCOL_SWITCH | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 3 = MODBUS,0=MSTP.
22 | 1 | MODBUS_NET_STATUS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | LED instruction (for HUM_RS485 and CO2_RS485),0=old hearbeat way, (not 0) = new communiction way
23 | 1 | MODBUS_BLIP_GAP | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | blip gap of led (for HUM_RS485 and CO2_RS485) when led instruciton is new way, defaut value is 3s
37 | 1 | MODBUS_INSTANCE_LOWORD | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | BACNET_INSTANCE_LOWORD
38 | 1 | MODBUS_INSTANCE_HIWORD | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | BACNET_INSTANCE_HIWORD
39 | 1 | MODBUS_STATION_NUMBER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | BACNET_STATION_NUMBER
40 | 1 | MODBUS_MAC_ADDRESS_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
41 | 1 | MODBUS_MAC_ADDRESS_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
42 | 1 | MODBUS_MAC_ADDRESS_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
43 | 1 | MODBUS_MAC_ADDRESS_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
44 | 1 | MODBUS_MAC_ADDRESS_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
45 | 1 | MODBUS_MAC_ADDRESS_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
46 | 1 | MODBUS_IP_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=static IP; 1= DHCP
47 | 1 | MODBUS_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
48 | 1 | MODBUS_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
49 | 1 | MODBUS_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
50 | 1 | MODBUS_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
51 | 1 | MODBUS_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
52 | 1 | MODBUS_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
53 | 1 | MODBUS_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
54 | 1 | MODBUS_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
55 | 1 | MODBUS_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
56 | 1 | MODBUS_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
57 | 1 | MODBUS_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
58 | 1 | MODBUS_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
61 | 1 | MODBUS_GHOST_IP_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_MODE
62 | 1 | MODBUS_GHOST_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
63 | 1 | MODBUS_GHOST_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
64 | 1 | MODBUS_GHOST_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
65 | 1 | MODBUS_GHOST_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
66 | 1 | MODBUS_GHOST_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
67 | 1 | MODBUS_GHOST_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
68 | 1 | MODBUS_GHOST_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
69 | 1 | MODBUS_GHOST_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
70 | 1 | MODBUS_GHOST_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
71 | 1 | MODBUS_GHOST_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
72 | 1 | MODBUS_GHOST_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
73 | 1 | MODBUS_GHOST_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
75 | 1 | MODBUS_GHOST_LISTEN_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | GHOST_LISTEN_PORT
76 | 1 | MODBUS_WRITE_GHOST_SYSTEM | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 1=WRITE_GHOST_SYSTEM
201 | 1 | MODBUS_TEMPERATURE_DEGREE_C_OR_F | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Temperature display unit ,0= CELSIUS DEGREE , 1= FAHRENHEIT DEGREE
204 | 1 | MODBUS_TEMPERATURE_CELSIUS | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | Temperature at celsius
205 | 1 | MODBUS_TEMPERATURE_FAHRENHEIT | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | Temperature at fahrenheit
207 | 1 | MODBUS_HUMIDITY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer/10 | RH humidity
210 | 1 | MODBUS_CO2_INTERNAL_EXIST | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | internal_co2_module_type, NONE ->0 , MAYBE_OGM200 ->1 , MAYBE_TEMCO_CO2 ->2 , OGM200 ->3 , TEMCO_CO2 ->4 , SCD30 ->5 , MH_Z19B-> 6
211 | 1 | MODBUS_CO2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CO2
212 | 1 | MODBUS_CO2_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | CO2 offset
213 | 1 | MODBUS_CO2_PREALARM_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 previous alarm setpoint
214 | 1 | MODBUS_CO2_ALARM_SETPOINT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 alarm setpoint
1232 | 1 | MODBUS_CO2_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | CO2 filter
1239 | 1 | MODBUS_RTC_YEAR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | YEAR
1240 | 1 | MODBUS_RTC_MONTH | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | MONTH
1241 | 1 | MODBUS_RTC_DAY | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | DAY
1242 | 1 | MODBUS_RTC_WEEK | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WEEK
1243 | 1 | MODBUS_RTC_HOUR | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | HOUR
1244 | 1 | MODBUS_RTC_MINUTE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | MINUTE
1245 | 1 | MODBUS_RTC_SECOND | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SECOND
1255 | 1 | MODBUS_OUTPUT_RANGE_MIN_TEM | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | Temperature output range MIX default value:0℃
1256 | 1 | MODBUS_OUTPUT_RANGE_MAX_TEM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Temperature output range MAX default value:100℃
1257 | 1 | MODBUS_OUTPUT_RANGE_MIN_HUM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer/10 | Humidity output range MIX default value: 0% RH
1258 | 1 | MODBUS_OUTPUT_RANGE_MAX_HUM | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer/10 | Humidity output range MAX default value: 100% RH
1259 | 1 | MODBUS_OUTPUT_RANGE_MIN_CO2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 output range MIX default value: 0 PPM
1260 | 1 | MODBUS_OUTPUT_RANGE_MAX_CO2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 output range MAX default value: 2000 PPM
1262 | 1 | MODBUS_BACKLIGHT_KEEP_SECONDS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0:OFF , 255:ON , 1--254 :Backlight ON Timer left
3001 | 1 | MODBUS_TEMPRATURE_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | TEMPRATURE FILTER
3002 | 1 | MODBUS_HUIDITY_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | HUMIDITY FILTER
3049 | 1 | MODBUS_DEW_PT | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | unit.℃
3050 | 1 | MODBUS_DEW_PT_F | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | unit.℉
3053 | 1 | MODBUS_PWS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | unit.hPa
3054 | 1 | MODBUS_MIX_RATIO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | unit.g/kg
3055 | 1 | MODBUS_ENTHALPY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | unit.kJ/kg
3056 | 1 | MODBUS_TEMP_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | TEMPERATURE OFFSET
3057 | 1 | MODBUS_HUM_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | HUMIDITY OFFSET
3066 | 1 | MODBUS_OUTPUT_HUM | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer/100 | HUMIDITY OUTPUT 0-10 volts
3067 | 1 | MODBUS_OUTPUT_TEMP | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer/100 | TEMPERATURE OUTPUT 0-10 volts
3068 | 1 | MODBUS_OUTPUT_CO2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer/100 | CO2 OUTPUT 0-10 volts
3070 | 1 | MODBUS_OUTPUT_HUM_VOL_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | HUMIDITY VOLTAGE OFFSET
3071 | 1 | MODBUS_OUTPUT_TEMP_VOL_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | TEMPERATURE VOLTAGE OFFSET
3072 | 1 | MODBUS_OUTPUT_CO2_VOL_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | CO2 VOLTAGE OFFSET
3073 | 1 | MODBUS_OUTPUT_HUM_CUR_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | HUMIDITY CURRENT OFFSET
3074 | 1 | MODBUS_OUTPUT_TEMP_CUR_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | TEMPERATURE CURRENT OFFSET
3075 | 1 | MODBUS_OUTPUT_CO2_CUR_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | CO2 CURRENT OFFSET
3141 | 1 | MODBUS_CO2_FORCED_RE-CALIBRATION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Sensirion CO2 sensor RE-CALIBRATION : Locate the device in an environment with air having a stable CO2 concentration in the range of 400 ppm to 2000 ppm. 1. Setting and controlling a known CO2 concentration in a sealed environment with the set CO2concentration acting as the reference value for FRC . 2.Fresh air from the outside can be used as a reference. Outside air typically has a CO2 concentration of 400 ppm . expose the device to outside air, e.g. by placing it close to an open window or outside. Direct sun light, extreme temperatures,and strong air flow have to be prevented,After 5 minutes, apply FRC with the reference value 400 ppm .

## AirLab-ESP
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | Serial Number - 4 byte value. Read-only
4 | 1 | MODBUS_VERSION_NUMBER_LO | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | firmware Version low. Read-only
5 | 1 | MODBUS_FIRMWARE_VERSION_HIGH | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version high
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Product Model. This is a read-only register that is used by the microcontroller to determine the product
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version
12 | 1 | MODBUS_BAUDRATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | UART_1200 = 0, UART_2400 = 1, UART_3600 = 2, UART_4800 = 3, UART_7200 = 4, UART_9600 = 5, UART_19200 = 6, UART_38400 = 7, UART_57600 = 8, UART_115200 = 9, UART_921600 = 10
14 | 1 | ISP_VER | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | bootloader revison
16 | 1 | MODBUS_UPDATE_STATUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Firmware Update Register, used to show the status of firmware updates.Writing 143 sets the config back to out of the box except for Modbus ID and baud rate. Write 159 to fix the current config as the user defaults, this is done automatically by T3000
19 | 1 | UART CONFIG | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Protocol setting , NOUSE = 0, MODBUS = 2, BACNET = 9,
32 | 1 | MODBUS_INSTANCE_HI | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | High word of instance number
34 | 1 | MODBUS_MINI_TYPE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Sub device type, 15->airlab
35 | 1 | MODBUS_INSTANCE_LO | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Low word of instance number
36 | 1 | MODBUS_PANEL_NUMBER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Panel number
42 | 1 | MODBUS_STATION_NUM | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Station NUM of mstp commucnication
46 | 1 | MODBUS_NETWORK_NUMBER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | NETWORK_NUMBER
2001 | 1 | MODBUS_WIFI_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI IP MODE , 0-DHCP,1-STATIC
2004 | 1 | MODBUS_WIFI_MODBUS_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WIFI_MODBUS_PORT ,Default value :502
2005 | 1 | MODBUS_WIFI_BACNET_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | BACnet PORT , Default value :47808
2010 | 32 | MODBUS_WIFI_SSID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | WIFI_SSID
2042 | 16 | MODBUS_WIFI_PASSWORD | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | WIFI_PASSWORD
2058 | 1 | MODBUS_WIFI_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2059 | 1 | MODBUS_WIFI_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2060 | 1 | MODBUS_WIFI_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2061 | 1 | MODBUS_WIFI_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2062 | 1 | MODBUS_WIFI_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2063 | 1 | MODBUS_WIFI_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2064 | 1 | MODBUS_WIFI_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2065 | 1 | MODBUS_WIFI_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2066 | 1 | MODBUS_WIFI_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2067 | 1 | MODBUS_WIFI_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2068 | 1 | MODBUS_WIFI_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2069 | 1 | MODBUS_WIFI_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2070 | 1 | MODBUS_WIFI_MAC_ADDRESS_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2071 | 1 | MODBUS_WIFI_MAC_ADDRESS_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2072 | 1 | MODBUS_WIFI_MAC_ADDRESS_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2073 | 1 | MODBUS_WIFI_MAC_ADDRESS_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2074 | 1 | MODBUS_WIFI_MAC_ADDRESS_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2075 | 1 | MODBUS_WIFI_MAC_ADDRESS_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
50104 | 1 | DEGC_OR_F | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Temperature units , 0 = DegC, 1 = DegF
50121 | 1 | MODBUS_TEMPRATURE | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | TEMPERATURE reading in DegC or F from the sensor
50139 | 1 | MODBUS_CO2_SENSOR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 value ,(Unit:ppm)
50140 | 1 | MODBUS_HUMIDITY_SENSOR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Relative humidity ( % )
50142 | 1 | MODBUS_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Temperature filter
50151 | 1 | MODBUS_CO2_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 filer
50152 | 1 | MODBUS_HUMIDITY_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | HUM filer
50153 | 1 | MODBUS_TEMPRATURE_CALIBARATION_DATA | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | temperature calibration offset
50434 | 1 | MODBUS_LCD_BACKLIGHT_TURN_ON_TIME | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Backlight ON timer ,Valid Value 0-255 ,Unit: minute(s) , 0 = always OFF , 255=always ON, 1-254: Backlight on timer left
50612 | 1 | MODBUS_CO2_CALIBRATION_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 CALIBRATION OFFSET
50613 | 1 | MODBUS_SOUND_TRIGGER VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | SOUND TRIGGER VALUE
50614 | 1 | MODBUS_SOUND_TIMER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | SOUND TIMER (Unit:minute)
50615 | 1 | MODBUS_SOUND_ALARM_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | SOUND ALARM 1:ON , 0:OFF
50616 | 1 | MODBUS_SOUND_TIME_LEFT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | SOUND ALARM ON TIME LEFT
50617 | 1 | MODBUS_LIGHT_TRIGGER VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | LIGHT TRIGGER VALUE
50618 | 1 | MODBUS_LIGHT_TIMER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | LIGHT TIMER (Unit:minute)
50619 | 1 | MODBUS_LIGHT_ALARM_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | LIGHT ALARM 1: ON 0:OFF
50620 | 1 | MODBUS_LIGHT_TIME_LEFT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | LIGHT ALARM ON TIME LEFT
50621 | 1 | MODBUS_CO2_TRIGGER VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 TRIGGER VALUE
50622 | 1 | MODBUS_CO2_TIMER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 TIMER (Unit:minute)
50623 | 1 | MODBUS_CO2_ALARM_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CO2_ALARM 1:ON , 0:OFF
50624 | 1 | MODBUS_CO2_TIME_LEFT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CO2 ALARM ON TIME LEFT
50628 | 1 | MODBUS_LIGHT_SENSOR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | value of light sensor,(Unit:lux)
50629 | 1 | MODBUS_PIR_SELECT_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PIR sensor select 1=PIR sensor enable 0=PIR sensor disable
50630 | 1 | MODBUS_PIR_REAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIR sensor REAL value ,
50631 | 1 | MODBUS_PIR_THRESHOLD | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PIR sensor ZERO value ,Stable ADC reference value when it is not triggered .
50633 | 1 | MODBUS_PIR_TRIGGER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OCC_TRIGGER value = Absolute(REAL value - ZERO value ) , set threshold for pir sensor, default:30
50634 | 1 | MODBUS_PIR_TRIGGER_TIMER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OCC_TRIGGER TIMER(Unit:minute)
50635 | 1 | MODBUS_PIR_ALARM_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1 :ALARM ON , 0 : ALARM OFF
50636 | 1 | MODBUS_PIR_TIME_LEFT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | ALARM ON TIME LEFT
50640 | 1 | MODBUS_SOUND_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Sound sensor real value, (Unit:dbm )
50736 | 1 | MODBUS_PIR_STATUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 1=occupied, 0=unoccupied
50760 | 1 | MODBUS_PM1.0_WEIGHT_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM1.0 real value, unit : ug/m3
50761 | 1 | MODBUS_PM2.5_WEIGHT_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM2.5 real value, unit : ug/m3
50762 | 1 | MODBUS_PM4.0_WEIGHT_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM4.0 real value, unit : ug/m3
50763 | 1 | MODBUS_PM10_WEIGHT_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM10 real value, unit : ug/m3
50764 | 1 | MODBUS_PM0.5_NUMBER_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM0.5 real value, unit number
50765 | 1 | MODBUS_PM1.0_NUMBER_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM1.0 real value, unit number
50766 | 1 | MODBUS_PM2.5_NUMBER_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM2.5 real value, unit number
50767 | 1 | MODBUS_PM4.0_NUMBER_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM4.0 real value, unit number
50768 | 1 | MODBUS_PM10_NUMBER_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM10 real value, unit number
50769 | 1 | MODBUS_HUM_CALIBRATION_DATA | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Humidity calibration offset
50988 | 1 | MODBUS_VOC_SENSIRION_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Tvoc sensor real value,(Unit:ppb )
50994 | 1 | MODBUS_WBGT | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | Wet bulb globe temperature WBGT is an experimental forecast tool indicating expected heat stress on the human body when in direct sunlight. It estimates the effect of temperature, relative humidity, wind speed, and solar radiation on humans using a combination of temperatures from three thermometers A Wet bulb measures the temperature read by a thermometer covered in a wet cloth. As water evaporates from the cloth, evaporation cools the thermometer. This mirrors how the human body cools itself with sweat. A black globe is used to measure solar radiation. Solar radiation heats the globe and wind blowing across it cools the globe. A Dry bulb calculates the air temperature measured in the shade. It is the temperature you would see on your thermometer outside. With WBGT forecasts available by region up to 7 days in advance, it is a useful tool for planning ahead.
51020 | 1 | CO2_SENSOR_TURN_ON_TIME | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | CO2_TURN_ON_TIME
51021 | 1 | CO2_SENSOR_TURN_OFF_TIME | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | CO2_TURN_OFF_TIME
51022 | 1 | PM_SENSOR_TURN_ON_TIME | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | PM_TURN_ON_TIME
51023 | 1 | PM_SENSOR_TURN_OFF_TIME | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | PM_TURN_OFF_TIME
51951 | 1 | MODBUS_CO2_FORCED_RE-CALIBRATION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Locate the device in an environment with air having a stable CO2 concentration in the range of 400 ppm to 2000 ppm. 1. Setting and controlling a known CO2 concentration in a sealed environment with the set CO2concentration acting as the reference value for FRC . 2.Fresh air from the outside can be used as a reference. Outside air typically has a CO2 concentration of 400 ppm . expose the device to outside air, e.g. by placing it close to an open window or outside. Direct sun light, extreme temperatures, and strong air flow have to be prevented,After 5 minutes, apply FRC with the reference value 400 ppm .
51954 | 1 | MODBUS_DISPLAY_CONFIG5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the fifth line config. Value 5 show PM2.5 in line 5 , value 20 show nothing in line 5.
51955 | 1 | MODBUS_IS_BLANK_SCREEN | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0 - default normal display 1 -> blank screen
51956 | 1 | MODBUS_DISPLAY_CONFIG1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the first line config. 0->temperature, 1->humidity, 2->co2 , 3->voc , 20-> none
51957 | 1 | MODBUS_DISPLAY_CONFIG2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the second line config. 0->temperature, 1->humidity, 2->co2 , 3->voc , 20-> none
51958 | 1 | MODBUS_DISPLAY_CONFIG3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the third line config. 0->temperature, 1->humidity, 2->co2 , 3->voc , 20-> none
51959 | 1 | MODBUS_DISPLAY_CONFIG4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the forth line config. 0->temperature, 1->humidity, 2->co2 , 3->voc , 20-> none

## AirLab
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description | Unit
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | Serial Number - 4 byte value. Read-only
4 | 2 | MODBUS_VERSION_NUMBER_LO | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | Software Version – 2 byte value. Read-only
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Product Model. This is a read-only register that is used by the microcontroller to determine the product
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version
11 | 1 | MODBUS_ADDRESS_PLUG_N_PLAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
15 | 1 | MODBUS_BAUDRATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0=9600,1=19200,2=38400,3=57600,4=115200,5=76800
16 | 1 | MODBUS_UPDATE_STATUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Firmware Update Register, used to show the status of firmware updates.Writing 143 sets the config back to out of the box except for Modbus ID and baud rate. Write 159 to fix the current config as the user defaults, this is done automatically by T3000
21 | 1 | MODBUS_BACNET_SWITCH | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Protocol setting , 0 = Modbus , 1 = BACnet
101 | 1 | MODBUS_FIR_AMBIENT_TEMPERATURE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Ambient temperature from FIR sensor
102 | 1 | MODBUS_FIR_OBJECT_TEMPERATURE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Object temperature from FIR sensor
104 | 1 | DEGC_OR_F | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Temperature units , 0 = DegC, 1 = DegF
121 | 1 | MODBUS_TEMPRATURE | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | TEMPERATURE reading in DegC or F from the sensor
139 | 1 | MODBUS_CO2_SENSOR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 value ,(Unit:ppm)
140 | 1 | MODBUS_HUMIDITY_SENSOR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Relative humidity ( % )
142 | 1 | MODBUS_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Temperature filter
151 | 1 | MODBUS_CO2_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 filer
152 | 1 | MODBUS_HUMIDITY_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | HUM filer
153 | 1 | MODBUS_TEMPRATURE_CALIBARATION_DATA | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | temperature calibration offset
434 | 1 | MODBUS_LCD_BACKLIGHT_TURN_ON_TIME | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Backlight ON timer ,Valid Value 0-255 ,Unit: minute(s) , 0 = always OFF , 255=always ON, 1-254: Backlight on timer left
612 | 1 | MODBUS_CO2_CALIBRATION_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 CALIBRATION OFFSET
613 | 1 | MODBUS_SOUND_TRIGGER VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | SOUND TRIGGER VALUE
614 | 1 | MODBUS_SOUND_TIMER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | SOUND TIMER (Unit:minute)
615 | 1 | MODBUS_SOUND_ALARM_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | SOUND ALARM 1:ON , 0:OFF
616 | 1 | MODBUS_SOUND_TIME_LEFT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | SOUND ALARM ON TIME LEFT
617 | 1 | MODBUS_LIGHT_TRIGGER VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | LIGHT TRIGGER VALUE
618 | 1 | MODBUS_LIGHT_TIMER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | LIGHT TIMER (Unit:minute)
619 | 1 | MODBUS_LIGHT_ALARM_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | LIGHT ALARM 1: ON 0:OFF
620 | 1 | MODBUS_LIGHT_TIME_LEFT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | LIGHT ALARM ON TIME LEFT
621 | 1 | MODBUS_CO2_TRIGGER VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 TRIGGER VALUE
622 | 1 | MODBUS_CO2_TIMER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | CO2 TIMER (Unit:minute)
623 | 1 | MODBUS_CO2_ALARM_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CO2_ALARM 1:ON , 0:OFF
624 | 1 | MODBUS_CO2_TIME_LEFT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | CO2 ALARM ON TIME LEFT
628 | 1 | MODBUS_LIGHT_SENSOR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | value of light sensor,(Unit:lux)
629 | 1 | MODBUS_PIR_SELECT_ENABLE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PIR sensor select 1=PIR sensor enable 0=PIR sensor disable
630 | 1 | MODBUS_PIR_REAL_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIR sensor REAL value ,
631 | 1 | MODBUS_PIR_THRESHOLD | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | PIR sensor ZERO value ,Stable ADC reference value when it is not triggered .
633 | 1 | MODBUS_PIR_TRIGGER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OCC_TRIGGER value = Absolute(REAL value - ZERO value ) , set threshold for pir sensor, default:30
634 | 1 | MODBUS_PIR_TRIGGER_TIMER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | OCC_TRIGGER TIMER(Unit:minute)
635 | 1 | MODBUS_PIR_ALARM_ON | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1 :ALARM ON , 0 : ALARM OFF
636 | 1 | MODBUS_PIR_TIME_LEFT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | ALARM ON TIME LEFT
640 | 1 | MODBUS_SOUND_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Sound sensor real value, (Unit:dbm )
736 | 1 | MODBUS_PIR_STATUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 1=occupied, 0=unoccupied
760 | 1 | MODBUS_PM1.0_WEIGHT_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM1.0 real value, unit : ug/m3
761 | 1 | MODBUS_PM2.5_WEIGHT_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM2.5 real value, unit : ug/m3
762 | 1 | MODBUS_PM4.0_WEIGHT_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM4.0 real value, unit : ug/m3
763 | 1 | MODBUS_PM10_WEIGHT_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM10 real value, unit : ug/m3
764 | 1 | MODBUS_PM0.5_NUMBER_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM0.5 real value, unit number
765 | 1 | MODBUS_PM1.0_NUMBER_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM1.0 real value, unit number
766 | 1 | MODBUS_PM2.5_NUMBER_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM2.5 real value, unit number
767 | 1 | MODBUS_PM4.0_NUMBER_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM4.0 real value, unit number
768 | 1 | MODBUS_PM10_NUMBER_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PM10 real value, unit number
769 | 1 | MODBUS_HUM_CALIBRATION_DATA | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Humidity calibration offset
988 | 1 | MODBUS_VOC_SENSIRION_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Tvoc sensor real value,(Unit:ppb )
994 | 1 | MODBUS_WBGT | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | Wet bulb globe temperature WBGT is an experimental forecast tool indicating expected heat stress on the human body when in direct sunlight. It estimates the effect of temperature, relative humidity, wind speed, and solar radiation on humans using a combination of temperatures from three thermometers A Wet bulb measures the temperature read by a thermometer covered in a wet cloth. As water evaporates from the cloth, evaporation cools the thermometer. This mirrors how the human body cools itself with sweat. A black globe is used to measure solar radiation. Solar radiation heats the globe and wind blowing across it cools the globe. A Dry bulb calculates the air temperature measured in the shade. It is the temperature you would see on your thermometer outside. With WBGT forecasts available by region up to 7 days in advance, it is a useful tool for planning ahead.
1020 | 1 | CO2_SENSOR_TURN_ON_TIME | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | CO2_TURN_ON_TIME
1021 | 1 | CO2_SENSOR_TURN_OFF_TIME | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | CO2_TURN_OFF_TIME
1022 | 1 | PM_SENSOR_TURN_ON_TIME | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | PM_TURN_ON_TIME
1023 | 1 | PM_SENSOR_TURN_OFF_TIME | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | PM_TURN_OFF_TIME
1951 | 1 | MODBUS_CO2_FORCED_RE-CALIBRATION | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Locate the device in an environment with air having a stable CO2 concentration in the range of 400 ppm to 2000 ppm. 1. Setting and controlling a known CO2 concentration in a sealed environment with the set CO2concentration acting as the reference value for FRC . 2.Fresh air from the outside can be used as a reference. Outside air typically has a CO2 concentration of 400 ppm . expose the device to outside air, e.g. by placing it close to an open window or outside. Direct sun light, extreme temperatures, and strong air flow have to be prevented,After 5 minutes, apply FRC with the reference value 400 ppm .
1954 | 1 | MODBUS_DISPLAY_CONFIG5 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the fifth line config. Value 5 show PM2.5 in line 5 , value 20 show nothing in line 5.
1955 | 1 | MODBUS_IS_BLANK_SCREEN | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0 - default normal display 1 -> blank screen
1956 | 1 | MODBUS_DISPLAY_CONFIG1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the first line config. 0->temperature, 1->humidity, 2->co2 , 3->voc , 20-> none
1957 | 1 | MODBUS_DISPLAY_CONFIG2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the second line config. 0->temperature, 1->humidity, 2->co2 , 3->voc , 20-> none
1958 | 1 | MODBUS_DISPLAY_CONFIG3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the third line config. 0->temperature, 1->humidity, 2->co2 , 3->voc , 20-> none
1959 | 1 | MODBUS_DISPLAY_CONFIG4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | the forth line config. 0->temperature, 1->humidity, 2->co2 , 3->voc , 20-> none
2001 | 1 | MODBUS_WIFI_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI IP MODE , 0-DHCP,1-STATIC
2004 | 1 | MODBUS_WIFI_MODBUS_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WIFI_MODBUS_PORT ,Default value :502
2005 | 1 | MODBUS_WIFI_BACNET_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | BACnet PORT , Default value :47808
2010 | 32 | MODBUS_WIFI_SSID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | WIFI_SSID
2042 | 16 | MODBUS_WIFI_PASSWORD | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | WIFI_PASSWORD
2058 | 1 | MODBUS_WIFI_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2059 | 1 | MODBUS_WIFI_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2060 | 1 | MODBUS_WIFI_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2061 | 1 | MODBUS_WIFI_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2062 | 1 | MODBUS_WIFI_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2063 | 1 | MODBUS_WIFI_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2064 | 1 | MODBUS_WIFI_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2065 | 1 | MODBUS_WIFI_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2066 | 1 | MODBUS_WIFI_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2067 | 1 | MODBUS_WIFI_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2068 | 1 | MODBUS_WIFI_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2069 | 1 | MODBUS_WIFI_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2070 | 1 | MODBUS_WIFI_MAC_ADDRESS_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2071 | 1 | MODBUS_WIFI_MAC_ADDRESS_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2072 | 1 | MODBUS_WIFI_MAC_ADDRESS_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2073 | 1 | MODBUS_WIFI_MAC_ADDRESS_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2074 | 1 | MODBUS_WIFI_MAC_ADDRESS_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2075 | 1 | MODBUS_WIFI_MAC_ADDRESS_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS

## Transducer2
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
10 | 1 | MODBUS_PROTOCOL | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0…modbus, 1…bancet
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | baudrate 0:9600 1:19200 2:38400 3:57600 4:115200
17 | 1 | MODBUS_SWITCH_OUTPUT_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 1=0…10V, 0=4…20mA
18 | 1 | MODBUS_SWITCH_TEMP_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=0-100c,1=-20…80c,2=0…50c,3=-50…50c,4=-20…140f,5=0…100f,6=40…90f,7=-40…140f
20 | 1 | MODBUS_SWITCH_HUMI_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=dewPoint, 1=enthalpy, 2=absolute humidity,3=real humidity
21 | 1 | MODBUS_TEMPERATURE_UNIT | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=Celsius,1=Fahrenheit
25 | 1 | MODBUS_IS_CO2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=CO2 inexist,1=CO2 exist
35 | 1 | MODBUS_TEMPERATURE_OFFSET | 03_06 Read Holding and Write Single | 8 Bit Signed Integer | Offset of temperature
36 | 1 | MODBUS_HUMIDITY_OFFSET | 03_06 Read Holding and Write Single | 8 Bit Signed Integer | Offset of humidty
37 | 1 | MODBUS_TEMPERATURE_C | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | temperature (uint C)
38 | 1 | MODBUS_TEMPERATURE_F | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | temperature (uint F)
39 | 1 | MODBUS_HUMIDITY | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | Humdity
41 | 1 | MODBUS_DEWPOINT | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | dew point
42 | 1 | MODBUS_ENTHALPY | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | enthalpy
44 | 1 | MODBUS_ABSOLUTE_HUMI | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | absolute humidity
64 | 1 | MODBUS_DEF_CUSTOMER_CO2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | for co2,default scale or customized, 0: default , 1: customized
65 | 1 | MODBUS_CURRENT_MIN_CO2 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for co2,the minimum currnet of customiezed scale
66 | 1 | MODBUS_CURRENT_MAX_CO2 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for co2,the maximum currnet of customiezed scale
67 | 1 | MODBUS_VOLTAGE_MIN_CO2 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for co2,the minimum voltage of customiezed scale
68 | 1 | MODBUS_VOLTAGE_MAX_CO2 | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for co2,the maximum voltage of customiezed scale
69 | 2 | MODBUS_CO2_MIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the minimum co2 of customiezed scale
70 | 2 | MODBUS_CO2_MAX | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the maximum co2 of customiezed scale
71 | 1 | MODBUS_OUTPUT_CUR_CO2 | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | for co2,vale of output current , You need to divide by 10. For example, 123 means 12.3 ma
72 | 1 | MODBUS_OUTPUT_VOL_CO2 | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | for co2,value of output voltage , You need to divide by 10. For example, 123 means 12.3 V
74 | 2 | MODBUS_CO2 | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | for co2, co2 value
100 | 1 | MODBUS_DEF_CUSTOMER_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,default scale or customized, 0: default , 1: customized
101 | 1 | MODBUS_CURRENT_MIN_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,the minimum currnet of customiezed scale
102 | 1 | MODBUS_CURRENT_MAX_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,the maximum currnet of customiezed scale
103 | 1 | MODBUS_VOLTAGE_MIN_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,the minimum voltage of customiezed scale
104 | 1 | MODBUS_VOLTAGE_MAX_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,the maximum voltage of customiezed scale
105 | 2 | MODBUS_TEMP_MIN | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for temperature,the minimum temperature of customiezed scale
106 | 2 | MODBUS_TEMP_MAX | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for temperature,the maximum temperature of customiezed scale
107 | 1 | MODBUS_OUTPUT_CUR_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,vale of output current , You need to divide by 10. For example, 123 means 12.3 ma
108 | 1 | MODBUS_OUTPUT_VOL_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,value of output voltage , You need to divide by 10. For example, 123 means 12.3 V
110 | 1 | MODBUS_DEF_CUSTOMER_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,default scale or customized, 0: default , 1: customized
111 | 1 | MODBUS_CURRENT_MIN_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,the minimum currnet of customiezed scale
112 | 1 | MODBUS_CURRENT_MAX_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,the maximum currnet of customiezed scale
113 | 1 | MODBUS_VOLTAGE_MIN_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,the minimum voltage of customiezed scale
114 | 1 | MODBUS_VOLTAGE_MAX_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,the maximum voltage of customiezed scale
115 | 2 | MODBUS_HUM_MIN | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for humidity,the minimum pressure of customiezed scale
116 | 2 | MODBUS_HUM_MAX | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for humidity,the maximum pressure of customiezed scale
117 | 1 | MODBUS_OUTPUT_CUR_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,vale of output current , You need to divide by 10. For example, 123 means 12.3 ma
118 | 1 | MODBUS_OUTPUT_VOL_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,value of output voltage , You need to divide by 10. For example, 123 means 12.3 V

## MEx37
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
60 | 2 | METER_MODEL | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI
70 | 4 | SERIAL_NUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI
72 | 1 | FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Format: X.Y.Z
75 | 4 | DATE_TIME | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Year, Month/Day, Hour/Minute, Millisecond
80 | 1 | SLAVE_ADDRESS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1–247
81 | 1 | BAUD_RATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=2400, 1=4800, 2=9600, 3=19200, 4=38400, 5=57600, 6=115200
82 | 1 | PARITY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0=None, 1=Odd, 2=Even
83 | 1 | STOP_BIT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 1=1 bit, 2=2 bit
200 | 1 | RELAY_MODE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Relay output control mode: 0=Manual, 1=Alarm
201 | 1 | RELAY_CONTROL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Relay output control (0=Open, 1=Closed)
202 | 1 | RELAY_STATE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Relay output status
210 | 1 | DIGITAL_INPUT | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0=DI1 open, DI2 open; 1=DI1 closed...
220 | 1 | PHASE_SEQ_STATUS | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0=OK, 1=Volt err, 2=Curr err, 3=Both err
300 | 1 | INSTR_CODE | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction code register
301 | 1 | INSTR_PARAM_1 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 1
302 | 1 | INSTR_PARAM_2 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 2
303 | 1 | INSTR_PARAM_3 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 3
304 | 1 | INSTR_PARAM_4 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 4
305 | 1 | INSTR_PARAM_5 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 5
306 | 1 | INSTR_PARAM_6 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 6
307 | 1 | INSTR_PARAM_7 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 7
308 | 1 | INSTR_PARAM_8 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 8
309 | 1 | INSTR_PARAM_9 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 9
310 | 1 | INSTR_PARAM_10 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 10
311 | 1 | INSTR_PARAM_11 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 11
312 | 1 | INSTR_PARAM_12 | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction parameter 12
423 | 1 | INSTR_EXEC | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Instruction execute trigger
424 | 1 | EXEC_RESULT_CODE | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0=OK, 80=Invalid Code, etc.
425 | 1 | EXEC_RESULT_DETAIL | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Detailed result of execution
500 | 1 | WIRING_MODE | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0=3P4W_4CT, 1=3P4W_3CT, 2=3P3W_3CT, 3=3P3W_2CT, 4=1P3W, 5=1P2W
501 | 1 | GRID_FREQUENCY | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Grid frequency (50 or 60 Hz)
502 | 1 | NOMINAL_VOLTAGE | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Nominal voltage (VT ratio not included)
503 | 2 | VT_RATIO | 3 Read Holding Registers (4x) | UInt32 | Voltage transformer ratio (value / 10000)
505 | 2 | CT_RATIO | 3 Read Holding Registers (4x) | UInt32 | Current transformer ratio (value / 10000)
550 | 1 | PHASE_A_CT_DIRECTION | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Phase A current direction: 0=Positive (default), 1=Negative
551 | 1 | PHASE_B_CT_DIRECTION | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Phase B current direction: 0=Positive (default), 1=Negative
552 | 1 | PHASE_C_CT_DIRECTION | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Phase C current direction: 0=Positive (default), 1=Negative
553 | 1 | PHASE_A_CT_CHANNEL | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Phase A CT channel: 0=Ch1 (default), 1=Ch2, 2=Ch3
554 | 1 | PHASE_B_CT_CHANNEL | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Phase B CT channel: 0=Ch1, 1=Ch2 (default), 2=Ch3
555 | 1 | PHASE_C_CT_CHANNEL | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Phase C CT channel: 0=Ch1, 1=Ch2, 2=Ch3 (default)
600 | 1 | VOLTAGE_ZERO_DRIFT_SUPPRESS | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Current zero-drift suppression threshold = (Nominal Current × CT ratio) × (Value ÷ 100), default = 10
601 | 1 | CURRENT_ZERO_DRIFT_SUPPRESS | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Phase C CT channel: 0=Ch1, 1=Ch2, 2=Ch3 (default)
800 | 1 | CURRENT_TARIFF | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Current active tariff (0–5 = Tariff 1–6)
801 | 1 | TARIFF_SWITCH_MODE | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Tariff switching mode: 0 = Manual, 1 = RTC
802 | 1 | MANUAL_TARIFF_SELECT | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Manual selection of tariff (only valid when mode is manual)
803 | 3 | RTC_TA_START | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Start time of tariff segment TA
806 | 3 | RTC_TB_START | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Start time of tariff segment TB
809 | 3 | RTC_TC_START | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Start time of tariff segment TC
812 | 3 | RTC_TD_START | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Start time of tariff segment TD
815 | 3 | RTC_TE_START | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Start time of tariff segment TE
818 | 3 | RTC_TF_START | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Start time of tariff segment TF
821 | 1 | TA_TARIFF_SELECT | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Tariff selected for time segment TA (0–5 = Tariff 1–6)
822 | 1 | TB_TARIFF_SELECT | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Tariff selected for time segment TB
823 | 1 | TC_TARIFF_SELECT | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Tariff selected for time segment TC
824 | 1 | TD_TARIFF_SELECT | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Tariff selected for time segment TD
825 | 1 | TE_TARIFF_SELECT | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Tariff selected for time segment TE
826 | 1 | TF_TARIFF_SELECT | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Tariff selected for time segment TF
1000 | 2 | CURRENT_L1 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Phase L1 current
1002 | 2 | CURRENT_L2 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Phase L2 current
1004 | 2 | CURRENT_L3 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Phase L3 current
1006 | 2 | CURRENT_AVG | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Average current of L1–L3
1008 | 2 | CURRENT_N | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Neutral current
1010 | 2 | VOLTAGE_L1 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Phase L1 to Neutral
1012 | 2 | VOLTAGE_L2 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Phase L2 to Neutral
1014 | 2 | VOLTAGE_L3 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Phase L3 to Neutral
1016 | 2 | VOLTAGE_PHASE_AVG | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Average phase voltage
1020 | 2 | VOLTAGE_L1_L2 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Line voltage L1-L2
1022 | 2 | VOLTAGE_L2_L3 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Line voltage L2-L3
1024 | 2 | VOLTAGE_L3_L1 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Line voltage L3-L1
1026 | 2 | VOLTAGE_LINE_AVG | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Average line voltage
1028 | 2 | ACTIVE_POWER_L1 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L1 active power
1030 | 2 | ACTIVE_POWER_L2 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L2 active power
1032 | 2 | ACTIVE_POWER_L3 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L3 active power
1034 | 2 | ACTIVE_POWER_TOTAL | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Total active power
1036 | 2 | REACTIVE_POWER_L1 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L1 reactive power
1038 | 2 | REACTIVE_POWER_L2 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L2 reactive power
1040 | 2 | REACTIVE_POWER_L3 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L3 reactive power
1042 | 2 | REACTIVE_POWER_TOTAL | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Total reactive power
1044 | 2 | APPARENT_POWER_L1 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L1 apparent power
1046 | 2 | APPARENT_POWER_L2 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L2 apparent power
1048 | 2 | APPARENT_POWER_L3 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L3 apparent power
1050 | 2 | APPARENT_POWER_TOTAL | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Total apparent power
1052 | 2 | POWER_FACTOR_L1 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Power factor of L1
1054 | 2 | POWER_FACTOR_L2 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Power factor of L2
1056 | 2 | POWER_FACTOR_L3 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Power factor of L3
1058 | 2 | POWER_FACTOR_TOTAL | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Total power factor
1060 | 2 | DPF_L1 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Displacement power factor L1
1062 | 2 | DPF_L2 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Displacement power factor L2
1064 | 2 | DPF_L3 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Displacement power factor L3
1066 | 2 | DPF_TOTAL | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Total displacement power factor
1068 | 2 | FREQUENCY_L1 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Frequency L1
1070 | 2 | FREQUENCY_L2 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Frequency L2
1072 | 2 | FREQUENCY_L3 | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Frequency L3
1074 | 2 | FREQUENCY_TOTAL | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Average system frequency
2500 | 4 | EP1_IMP_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Phase L1 imported energy
2504 | 4 | EP2_IMP_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Phase L2 imported energy
2508 | 4 | EP3_IMP_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Phase L3 imported energy
2512 | 4 | EP_TOTAL_IMP_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Total imported energy
2516 | 4 | EP1_EXP_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Phase L1 exported energy
2520 | 4 | EP2_EXP_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Phase L2 exported energy
2524 | 4 | EP3_EXP_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Phase L3 exported energy
2528 | 4 | EP_TOTAL_EXP_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Total exported energy
2532 | 4 | REACTIVE_IMP_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Imported reactive energy
2536 | 4 | REACTIVE_EXP_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Exported reactive energy
2600 | 2 | EP1_IMP_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | L1 imported energy (U32)
2602 | 2 | EP2_IMP_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | L2 imported energy
2604 | 2 | EP3_IMP_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | L3 imported energy
2606 | 2 | EP_TOTAL_IMP_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Total imported energy
2608 | 2 | EP1_EXP_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | L1 exported energy
2610 | 2 | EP2_EXP_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | L2 exported energy
2612 | 2 | EP3_EXP_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | L3 exported energy
2614 | 2 | EP_TOTAL_EXP_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Total exported energy
2616 | 2 | REACTIVE_IMP_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Imported reactive energy
2618 | 2 | REACTIVE_EXP_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Exported reactive energy
2700 | 4 | ET1_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 1 energy (import)
2704 | 4 | ET2_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 2 energy
2708 | 4 | ET3_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 3 energy
2712 | 4 | ET4_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 4 energy
2716 | 4 | ET5_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 5 energy
2720 | 4 | ET6_INT64 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 6 energy
2750 | 2 | ET1_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 1 energy (U32 version)
2752 | 2 | ET2_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 2 energy
2754 | 2 | ET3_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 3 energy
2756 | 2 | ET4_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 4 energy
2758 | 2 | ET5_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 5 energy
2760 | 2 | ET6_U32 | 3 Read Holding Registers (4x) | 32 Bit Unsigned Integer HI_LO | Tariff 6 energy
3000 | 1 | DEMAND_METHOD | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0 = Sliding window, 1 = Fixed window
3001 | 1 | DEMAND_PERIOD | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Demand interval duration (seconds)
3002 | 1 | DEMAND_CUTOFF_TIME | 3 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Time window to discard short pulses
3020 | 2 | P1_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L1 active power demand
3022 | 2 | P2_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L2 active power demand
3024 | 2 | P3_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L3 active power demand
3026 | 2 | P_TOTAL_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Total active power demand
3028 | 2 | Q1_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L1 reactive power demand
3030 | 2 | Q2_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L2 reactive power demand
3032 | 2 | Q3_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L3 reactive power demand
3034 | 2 | Q_TOTAL_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Total reactive power demand
3036 | 2 | S1_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L1 apparent power demand
3038 | 2 | S2_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L2 apparent power demand
3040 | 2 | S3_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | L3 apparent power demand
3042 | 2 | S_TOTAL_DEMAND | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Total apparent power demand
4000 | 2 | I1_THD | 3 Read Holding Registers (4x) | Floating HI_LO/10 | THD% of current L1
4002 | 2 | I2_THD | 3 Read Holding Registers (4x) | Floating HI_LO/10 | THD% of current L2
4004 | 2 | I3_THD | 3 Read Holding Registers (4x) | Floating HI_LO/10 | THD% of current L3
4006 | 2 | U1_THD | 3 Read Holding Registers (4x) | Floating HI_LO/10 | THD% of voltage L1
4008 | 2 | U2_THD | 3 Read Holding Registers (4x) | Floating HI_LO/10 | THD% of voltage L2
4010 | 2 | U3_THD | 3 Read Holding Registers (4x) | Floating HI_LO/10 | THD% of voltage L3
6000 | 2 | I1_MAX | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Max current L1
6002 | 2 | I2_MAX | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Max current L2
6004 | 2 | I3_MAX | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Max current L3
6006 | 2 | I_TOTAL_MAX | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Max total current
6010 | 2 | U1_MAX | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Max voltage L1
6012 | 2 | U2_MAX | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Max voltage L2
6014 | 2 | U3_MAX | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Max voltage L3
6016 | 2 | U_LINE_MAX | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Max line voltage
6020 | 2 | I1_MIN | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Min current L1
6022 | 2 | I2_MIN | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Min current L2
6024 | 2 | I3_MIN | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Min current L3
6026 | 2 | I_TOTAL_MIN | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Min total current
6030 | 2 | U1_MIN | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Min voltage L1
6032 | 2 | U2_MIN | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Min voltage L2
6034 | 2 | U3_MIN | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Min voltage L3
6036 | 2 | U_LINE_MIN | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Min line voltage
7000 | 2 | U_NEG_UNBAL | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Voltage negative sequence unbalance
7002 | 2 | U_ZERO_UNBAL | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Voltage zero sequence unbalance
7004 | 2 | I_NEG_UNBAL | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Current negative sequence unbalance
7006 | 2 | I_ZERO_UNBAL | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Current zero sequence unbalance
8100 | 2 | U1_ANGLE | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Voltage phase angle of L1
8102 | 2 | U2_ANGLE | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Voltage phase angle of L2
8104 | 2 | U3_ANGLE | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Voltage phase angle of L3
8110 | 2 | I1_ANGLE | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Current phase angle of L1
8112 | 2 | UI1_ANGLE | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Voltage–Current angle L1
8114 | 2 | UI2_ANGLE | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Voltage–Current angle L2
8116 | 2 | UI3_ANGLE | 3 Read Holding Registers (4x) | Floating HI_LO/10 | Voltage–Current angle L3
10000 | 1 | ALARM_ENABLE_MAP1 | 3 Read Holding Registers (4x) | 8 Bit Unsigned Integer | Alarm enable bitmap for alarms 1–16 (bit N = 1 means enabled)
10001 | 1 | ALARM_ENABLE_MAP2 | 3 Read Holding Registers (4x) | 8 Bit Unsigned Integer | Alarm enable bitmap for alarms 17–32
10010 | 1 | ALARM_ACTIVE_MAP1 | 3 Read Holding Registers (4x) | 8 Bit Unsigned Integer | Alarm active status bitmap for alarms 1–16 (bit N = 1 means active)
10011 | 1 | ALARM_ACTIVE_MAP2 | 3 Read Holding Registers (4x) | 8 Bit Unsigned Integer | Alarm active status bitmap for alarms 17–32
10020 | 1 | ALARM_ACK_MAP1 | 3 Read Holding Registers (4x) | 8 Bit Unsigned Integer | Alarm acknowledgment map for alarms 1–16 (write 1 to acknowledge)
10021 | 1 | ALARM_ACK_MAP2 | 3 Read Holding Registers (4x) | 8 Bit Unsigned Integer | Alarm acknowledgment map for alarms 17–32

## HUM
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=9600,1=19200,2=38400,3=57600,4=115200,5=76800
21 | 1 | MODBUS_PROTOCOL_SWITCH | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 3 = MODBUS,0=MSTP.
37 | 1 | MODBUS_INSTANCE_LOWORD | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | BACNET_INSTANCE_LOWORD
38 | 1 | MODBUS_INSTANCE_HIWORD | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | BACNET_INSTANCE_HIWORD
39 | 1 | MODBUS_STATION_NUMBER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | BACNET_STATION_NUMBER
40 | 1 | MODBUS_MAC_ADDRESS_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
41 | 1 | MODBUS_MAC_ADDRESS_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
42 | 1 | MODBUS_MAC_ADDRESS_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
43 | 1 | MODBUS_MAC_ADDRESS_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
44 | 1 | MODBUS_MAC_ADDRESS_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
45 | 1 | MODBUS_MAC_ADDRESS_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
46 | 1 | MODBUS_IP_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=static IP; 1= DHCP
47 | 1 | MODBUS_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
48 | 1 | MODBUS_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
49 | 1 | MODBUS_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
50 | 1 | MODBUS_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
51 | 1 | MODBUS_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
52 | 1 | MODBUS_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
53 | 1 | MODBUS_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
54 | 1 | MODBUS_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
55 | 1 | MODBUS_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
56 | 1 | MODBUS_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
57 | 1 | MODBUS_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
58 | 1 | MODBUS_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
61 | 1 | MODBUS_GHOST_IP_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_MODE
62 | 1 | MODBUS_GHOST_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
63 | 1 | MODBUS_GHOST_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
64 | 1 | MODBUS_GHOST_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
65 | 1 | MODBUS_GHOST_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
66 | 1 | MODBUS_GHOST_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
67 | 1 | MODBUS_GHOST_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
68 | 1 | MODBUS_GHOST_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
69 | 1 | MODBUS_GHOST_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
70 | 1 | MODBUS_GHOST_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
71 | 1 | MODBUS_GHOST_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
72 | 1 | MODBUS_GHOST_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
73 | 1 | MODBUS_GHOST_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
75 | 1 | MODBUS_GHOST_LISTEN_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | GHOST_LISTEN_PORT
76 | 1 | MODBUS_WRITE_GHOST_SYSTEM | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 1=WRITE_GHOST_SYSTEM
100 | 1 | MODBUS_TEMPERATURE_FAHRENHEIT | 03 Read Holding Registers (4x) | 16 Bit Signed Integer | Temperature at fahrenheit
101 | 1 | MODBUS_TEMPERATURE_CELSIUS | 03 Read Holding Registers (4x) | 16 Bit Signed Integer | Temperature at celsius
121 | 1 | MODBUS_TEMPERATURE_DEGREE_C_OR_F | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Temperature display unit ,0= CELSIUS DEGREE , 1= FAHRENHEIT DEGREE
190 | 2 | MODBUS_HUM_FLOAT_ABCD | 03 Read Holding Registers (4x) | 32 Bit Float_ABCD | humidity for float_abcd
192 | 2 | MODBUS_TEMP_FLOAT_ABCD | 03 Read Holding Registers (4x) | 32 Bit Float_ABCD | temperature for float_abcd
287 | 1 | MODBUS_HUM_OUTPUT_RANGE_MIN_HUMIDITY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Humidity output range MIX default value: 0% RH
288 | 1 | MODBUS_HUM_OUTPUT_RANGE_MIN_HUMIDITY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Humidity output range MAX default value: 100% RH
304 | 1 | MODBUS_HUMIDITY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | RH humidity
450 | 1 | MODBUS_HUM_TEMP_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Teamperature_OFFSET
451 | 1 | MODBUS_HUM_HUMIDITY_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Humidity_OFFSET
452 | 1 | MODBUS_HUM_EXT_TEMPRATURE_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | TEMPRATURE_FILTER
453 | 1 | MODBUS_HUM_HUIDITY_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | HUIDITY_FILTER
482 | 1 | MODBUS_DEW_PT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | unit.C
483 | 1 | MODBUS_DEW_PT_F | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | unit.F
488 | 1 | MODBUS_PWS | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | unit.hPa
489 | 1 | MODBUS_MIX_RATIO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | unit.g/kg
490 | 1 | MODBUS_ENTHALPY | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | unit.kJ/kg
538 | 1 | MODBUS_HUM_LIGHT_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Light intensity unit:Lux
600 | 1 | MODBUS_AQ_VALUE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AQ value
601 | 1 | MODBUS_CELBRA_AIR1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | air calibation point1
602 | 1 | MODBUS_CELBRA_AIR2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | air calibation point2
603 | 1 | MODBUS_CELBRA_AIR3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | air calibation point3
604 | 1 | MODBUS_CELBRA_AIR4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | air calibation point4
605 | 1 | MODBUS_AQ_LEVEL0 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AQ level0 value
606 | 1 | MODBUS_AQ_LEVEL1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AQ level1 value
607 | 1 | MODBUS_AQ_LEVEL2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AQ level2 value
608 | 1 | MODBUS_MAX_AQ_VAL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | max AQ value
609 | 1 | MODBUS_CALIBRATION_AQ | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | AQ calibration value
3134 | 1 | MODBUS_SCREEN_AREA_1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | disply item of the first line (0 - temperature, 1 - humdity, 2 - co2, 3 - none, 4 - PM2.5, 5 - PRESSURE , 6 - PM10, 7 - AQI, 8 - LIGHT,10 - Temperature setpoint, 11 - Humdity setpoint, 12 - CO2 setpoint)
3135 | 1 | MODBUS_SCREEN_AREA_2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | disply item of the second line(0 - temperature, 1 - humdity, 2 - co2, 3 - none, 4 - PM2.5, 5 - PRESSURE , 6 - PM10, 7 - AQI, 8 - LIGHT,10 - Temperature setpoint, 11 - Humdity setpoint, 12 - CO2 setpoint)
3136 | 1 | MODBUS_SCREEN_AREA_3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | disply item of the third line(0 - temperature, 1 - humdity, 2 - co2, 3 - none, 4 - PM2.5, 5 - PRESSURE , 6 - PM10, 7 - AQI, 8 - LIGHT,10 - Temperature setpoint, 11 - Humdity setpoint, 12 - CO2 setpoint)
3138 | 1 | MODBUS_ENABLE_SCROLL | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | whether enalbe scrolling display

## AFS
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description | Unit
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
10 | 1 | MODBUS_PROTOCOL | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0…modbus, 1…bancet
12 | 1 | MODBUS_UART_PARITY | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0-PARITY_NONE,1-PARITY_ODD,2-PARITY_EVEN
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | baudrate 0:9600 1:19200 2:38400 3:57600 4:115200
17 | 1 | MODBUS_SWITCH_OUTPUT_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 1=0…10V, 0=4…20mA
18 | 1 | MODBUS_SWITCH_DP_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | if sensor is spd31(Reg29 = 60):0=0-50,1=0-100,2=0-250,3=0-500; spd33(Reg29 = 20):0=0-750,1=0-1000,2=0-1250,3=0-1500; unit:Pa
20 | 1 | MODBUS_SWITCH_HUMI_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=dewPoint, 1=enthalpy, 2=absolute humidity,3=real humidity
21 | 1 | MODBUS_TEMPERATURE_UNIT | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=Celsius,1=Fahrenheit
19 | 1 | MODBUS_SWITCH_RSP_TIME_RANGE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Sensor response time,4 sec or 10 sec
29 | 1 | MODBUS_WHICH_PRESS | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | Sensor select, spd31 value = 60, spd33 value = 20， AMP = 30,NO PRESSURE SENSOR = 0
34 | 2 | MODBUS_DIFF_PRESSURE_VALUE | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | The differential pressure value obtained by the sensor,unit: Pascal
35 | 1 | MODBUS_TEMPERATURE_OFFSET | 03_06 Read Holding and Write Single | 8 Bit Signed Integer | Offset of temperature
36 | 1 | MODBUS_HUMIDITY_OFFSET | 03_06 Read Holding and Write Single | 8 Bit Signed Integer | Offset of humidty
37 | 1 | MODBUS_TEMPERATURE_C | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | temperature (uint C) It is available only when the hardware version is greater than 5
38 | 1 | MODBUS_TEMPERATURE_F | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | temperature (uint F) (HW Version greater than 5)
39 | 1 | MODBUS_HUMIDITY | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | Humdity (HW Version greater than 5)
41 | 1 | MODBUS_DEWPOINT | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | dew point (HW Version greater than 5)
42 | 1 | MODBUS_ENTHALPY | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | enthalpy (HW Version greater than 5)
43 | 1 | MODBUS_ABSOLUTE_HUMI2 | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | absolute humidity of the second sensor
44 | 1 | MODBUS_ABSOLUTE_HUMI | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | absolute humidity (HW Version greater than 5)
45 | 1 | MODBUS_CHANNEL1_TEMP | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | temperature of channel1
46 | 1 | MODBUS_CHANNEL2_TEMP | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | temperature of channel2 （REG95 = 1, FOR PLC）
47 | 1 | MODBUS_CHANNEL3_TEMP | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | temperature of channel3 （REG95 = 1, FOR PLC）
48 | 1 | MODBUS_DEW_POINT2 | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | dew point of the 2nd sensor (HW Version greater than 5) （REG95 = 1, FOR PLC）
49 | 1 | MODBUS_ENTHALPY2 | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | enthalpy of the 2nd sensor (HW Version greater than 5)（REG95 = 1, FOR PLC）
57 | 2 | MODBUS_FLOW_LENGTH | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The length of the square channel, unit: cm
58 | 2 | MODBUS_FLOW_WIDTH | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The Width of the square channel, unit: cm
59 | 1 | MODBUS_FLOW_UNIT | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Flow unit, 0-m³/s, 1-ft³/min, 2-L/min
60 | 2 | MODBUS_FLOW_SPEED | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Velocity, unit 0.1m/s
61 | 2 | MODBUS_FLOW_HI | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | High 16 bits of the flow value
62 | 2 | MODBUS_FLOW_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Low 16 bits of the flow value
63 | 2 | MODBUS_FLOW_RADIUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The radius of the circular channel, unit: cm. When using a square channel, please make sure that this value is 0
64 | 1 | MODBUS_DEF_CUSTOMER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | default scale or customized, 0: default , 1: customized
65 | 1 | MODBUS_CURRENT_MIN | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | the minimum currnet of customiezed scale
66 | 1 | MODBUS_CURRENT_MAX | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | the maximum currnet of customiezed scale
67 | 1 | MODBUS_VOLTAGE_MIN | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | the minimum voltage of customiezed scale
68 | 1 | MODBUS_VOLTAGE_MAX | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | the maximum voltage of customiezed scale
69 | 2 | MODBUS_PASCAL_MIN | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the minimum pressure of customiezed scale
70 | 2 | MODBUS_PASCAL_MAX | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | the maximum pressure of customiezed scale
71 | 1 | MODBUS_OUTPUT_CUR | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | vale of output current , You need to divide by 10. For example, 123 means 12.3 ma
72 | 1 | MODBUS_OUTPUT_VOL | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | value of output voltage , You need to divide by 10. For example, 123 means 12.3 V
75 | 1 | MODBUS_TEMPERATURE2_C | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | Offset of 2nd temperature（REG95 = 1, FOR PLC）
76 | 1 | MODBUS_TEMPERATURE2_F | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | Offset of 2nd humidty （REG95 = 1, FOR PLC）
77 | 1 | MODBUS_TEMP_WITH_OFFSET2 | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | 2nd temperature (uint C) It is available only when the hardware version is greater than 5 （REG95 = 1, FOR PLC）
78 | 1 | MODBUS_TEMP_WITH_OFFSET_F2 | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | 2nd temperature (uint F) (HW Version greater than 5)（REG95 = 1, FOR PLC）
79 | 1 | MODBUS_HUMI2 | 03 Read Holding Registers (4x) | 16 Bit Signed Integer/10 | 2nd Humidity （REG95 = 1, FOR PLC）
92 | 1 | MODBUS_FLOW_SHAPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | The shape of the channel, 0: square; 1: round
93 | 1 | MODBUS_FLOW_SHAPE_UNIT | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | The unit of the length, width or radius of the channel shape. 0: Metric unit; 1: Imperial unit.
95 | 1 | MODBUS_SUB_PRODUCT | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | sub product, 1 - PLC
98 | 1 | MODBUS_HUM2_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Humdity type or 2nd sensor， 0 - no sensor, 2 - SHT3X, 3 - STH4X （REG95 = 1, FOR PLC）
99 | 1 | MODBUS_HUM_TYPE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Humdity type， 0 - no sensor, 2 - SHT3X, 3 - STH4X
100 | 1 | MODBUS_DEF_CUSTOMER_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,default scale or customized, 0: default , 1: customized
101 | 1 | MODBUS_CURRENT_MIN_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,the minimum currnet of customiezed scale
102 | 1 | MODBUS_CURRENT_MAX_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,the maximum currnet of customiezed scale
103 | 1 | MODBUS_VOLTAGE_MIN_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,the minimum voltage of customiezed scale
104 | 1 | MODBUS_VOLTAGE_MAX_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,the maximum voltage of customiezed scale
105 | 2 | MODBUS_TEMP_MIN | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for temperature,the minimum temperature of customiezed scale
106 | 2 | MODBUS_TEMP_MAX | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for temperature,the maximum temperature of customiezed scale
107 | 1 | MODBUS_OUTPUT_CUR_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,vale of output current , You need to divide by 10. For example, 123 means 12.3 ma
108 | 1 | MODBUS_OUTPUT_VOL_TEMP | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for temperature,value of output voltage , You need to divide by 10. For example, 123 means 12.3 V
110 | 1 | MODBUS_DEF_CUSTOMER_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,default scale or customized, 0: default , 1: customized
111 | 1 | MODBUS_CURRENT_MIN_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,the minimum currnet of customiezed scale
112 | 1 | MODBUS_CURRENT_MAX_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,the maximum currnet of customiezed scale
113 | 1 | MODBUS_VOLTAGE_MIN_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,the minimum voltage of customiezed scale
114 | 1 | MODBUS_VOLTAGE_MAX_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,the maximum voltage of customiezed scale
115 | 2 | MODBUS_HUM_MIN | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for humidity,the minimum pressure of customiezed scale
116 | 2 | MODBUS_HUM_MAX | 03_06 Read Holding and Write Single | 16 Bit Signed Integer/10 | for humidity,the maximum pressure of customiezed scale
117 | 1 | MODBUS_OUTPUT_CUR_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,vale of output current , You need to divide by 10. For example, 123 means 12.3 ma
118 | 1 | MODBUS_OUTPUT_VOL_HUM | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | for humidity,value of output voltage , You need to divide by 10. For example, 123 means 12.3 V

## FAN_MODULE
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | Serial Number - 4 byte value. Read-only
4 | 1 | MODBUS_VERSION_NUMBER_LO | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Software Version LOW– 2 byte value. Read-only
5 | 1 | MODBUS_VERSION_NUMBER_HIGH | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Software Version HIGH – 2 byte value. Read-only
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Product Model. This is a read-only register that is used by the microcontroller to determine the product
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version
16 | 1 | MODBUS_UPDATE_STATUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Firmware Update Register, used to show the status of firmware updates.Writing 143 sets the config back to out of the box except for Modbus ID and baud rate. Write 159 to fix the current config as the user defaults, this is done automatically by T3000
81 | 1 | MODBUS_DAC_OUTPUT | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | DAC output, 0-min, 255-max
82 | 1 | MODBUS_PWM_OUTPUT | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | PWM output,255-min, 0-max
83 | 1 | MODBUS_SPEED_TACH | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | rpm, fan speed counter, 1/min
85 | 1 | MODBUS_INPUT_VOLTAGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0-10V input port voltage, unit:mV
101 | 1 | MODBUS_FIR_AMBIENT_TEMPERATURE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Ambient temperature from FIR sensor
102 | 1 | MODBUS_FIR_OBJECT_TEMPERATURE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Object temperature from FIR sensor
121 | 1 | MODBUS_TEMPRATURE | 03_06 Read Holding and Write Single | Floating LO_HI/10 | TEMPERATURE reading in DegC or F from the sensor
140 | 1 | MODBUS_HUMIDITY_SENSOR | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Relative humidity ( % )
628 | 1 | MODBUS_LIGHT_SENSOR | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | value of light sensor,(Unit:lux)
988 | 1 | MODBUS_VOC_SENSIRION_VALUE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Tvoc sensor real value,(Unit:ppb )
2001 | 1 | MODBUS_WIFI_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | WIFI IP MODE , 0-DHCP,1-STATIC
2004 | 1 | MODBUS_WIFI_MODBUS_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | WIFI_MODBUS_PORT ,Default value :502
2005 | 1 | MODBUS_WIFI_BACNET_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | BACnet PORT , Default value :47808
2010 | 32 | MODBUS_WIFI_SSID | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | WIFI_SSID
2042 | 16 | MODBUS_WIFI_PASSWORD | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | WIFI_PASSWORD
2058 | 1 | MODBUS_WIFI_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2059 | 1 | MODBUS_WIFI_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2060 | 1 | MODBUS_WIFI_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2061 | 1 | MODBUS_WIFI_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
2062 | 1 | MODBUS_WIFI_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2063 | 1 | MODBUS_WIFI_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2064 | 1 | MODBUS_WIFI_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2065 | 1 | MODBUS_WIFI_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
2066 | 1 | MODBUS_WIFI_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2067 | 1 | MODBUS_WIFI_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2068 | 1 | MODBUS_WIFI_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2069 | 1 | MODBUS_WIFI_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
2070 | 1 | MODBUS_WIFI_MAC_ADDRESS_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2071 | 1 | MODBUS_WIFI_MAC_ADDRESS_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2072 | 1 | MODBUS_WIFI_MAC_ADDRESS_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2073 | 1 | MODBUS_WIFI_MAC_ADDRESS_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2074 | 1 | MODBUS_WIFI_MAC_ADDRESS_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
2075 | 1 | MODBUS_WIFI_MAC_ADDRESS_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS

## Pressure
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 2 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | firmware Version
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=9600,1=19200,2=38400,3=57600,4=115200,5=76800
21 | 1 | MODBUS_PROTOCOL_SWITCH | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 3 = MODBUS,0=MSTP.
37 | 1 | MODBUS_INSTANCE_LOWORD | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | BACNET_INSTANCE_LOWORD
38 | 1 | MODBUS_INSTANCE_HIWORD | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | BACNET_INSTANCE_HIWORD
39 | 1 | MODBUS_STATION_NUMBER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | BACNET_STATION_NUMBER
40 | 1 | MODBUS_MAC_ADDRESS_1 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
41 | 1 | MODBUS_MAC_ADDRESS_2 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
42 | 1 | MODBUS_MAC_ADDRESS_3 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
43 | 1 | MODBUS_MAC_ADDRESS_4 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
44 | 1 | MODBUS_MAC_ADDRESS_5 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
45 | 1 | MODBUS_MAC_ADDRESS_6 | 03 Read Holding Registers (4x) | 8 Bit Unsigned Integer | MAC_ADDRESS
46 | 1 | MODBUS_IP_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=static IP; 1= DHCP
47 | 1 | MODBUS_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
48 | 1 | MODBUS_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
49 | 1 | MODBUS_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
50 | 1 | MODBUS_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | IP_ADDRESS
51 | 1 | MODBUS_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
52 | 1 | MODBUS_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
53 | 1 | MODBUS_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
54 | 1 | MODBUS_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | SUBNET_MASK
55 | 1 | MODBUS_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
56 | 1 | MODBUS_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
57 | 1 | MODBUS_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
58 | 1 | MODBUS_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GATEWAY
61 | 1 | MODBUS_GHOST_IP_MODE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_MODE
62 | 1 | MODBUS_GHOST_IP_ADDRESS_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
63 | 1 | MODBUS_GHOST_IP_ADDRESS_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
64 | 1 | MODBUS_GHOST_IP_ADDRESS_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
65 | 1 | MODBUS_GHOST_IP_ADDRESS_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_IP_ADDRESS
66 | 1 | MODBUS_GHOST_SUBNET_MASK_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
67 | 1 | MODBUS_GHOST_SUBNET_MASK_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
68 | 1 | MODBUS_GHOST_SUBNET_MASK_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
69 | 1 | MODBUS_GHOST_SUBNET_MASK_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_SUBNET
70 | 1 | MODBUS_GHOST_GATEWAY_1 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
71 | 1 | MODBUS_GHOST_GATEWAY_2 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
72 | 1 | MODBUS_GHOST_GATEWAY_3 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
73 | 1 | MODBUS_GHOST_GATEWAY_4 | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | GHOST_GATEWAY
75 | 1 | MODBUS_GHOST_LISTEN_PORT | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | GHOST_LISTEN_PORT
76 | 1 | MODBUS_WRITE_GHOST_SYSTEM | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 1=WRITE_GHOST_SYSTEM
700 | 1 | MODBUS_PRESSURE_SENSOR_MODEL | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0=26PCF (0-100PSI), 1=26PCG (0-250PSI), 10 = MPXV7002(-8 ~ +8 inWC), 11=MPXV7007(-27 ~ +27 inWC), 20 = -1 ~ +1 inWC
701 | 1 | MODBUS_PRESSURE_UNIT | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | 0= in.water ,1= KPa ,2=psi ,3=mmHg.4=inHg, 5= kg/cm2 , 6= atmosphere ,7= bar ,8= Pa .
702 | 1 | MODBUS_PRESSURE_UNIT_DEFAULT | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Default pressure unit
703 | 1 | MODBUS_OUTPUT_RANGE_MIN_PRESSURE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Pressure analog Output MIX value
704 | 1 | MODBUS_OUTPUT_RANGE_MAX_PRESSURE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Pressure annalog Output MAX value
705 | 1 | MODBUS_PRESSURE_FILTER | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Pressure filter , default value = 5 .
710 | 1 | MODBUS_PREESURE_AD | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Pressure AD value (FOR PS8,PS100 and PS250 )
711 | 1 | MODBUS_PRESSURE_VALUE_ORG | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Pressure value
712 | 1 | MODBUS_PRESSURE_VALUE_ORG_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Pressure value offset
836 | 1 | MODBUS_PRESSURE_BACKLIGHT_KEEP_SECONDS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | unit:second , 255=always ON , 0= always OFF

## CS
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 1 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version High
5 | 1 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version Low
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
11 | 1 | MODBUS_SENSOR_TYPE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | 0 = 0~50A, 1=0~100A, 2=0~200A, 3=300A
100 | 1 | MODBUS_CURRENT | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
101 | 1 | MODBUS_VOLTAGE | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer
134 | 1 | MODBUS_CURRENT_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The default value is 0. Changing this item offsets the value of register 100
135 | 1 | MODBUS_VOL_OFFSET | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | The default value is 0. Changing this item offsets the value of register 101
136 | 1 | MODBUS_CURRENT_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | value range ：0 - 10
137 | 1 | MODBUS_VOLTAGE_FILTER | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | value range ：0 - 10
141 | 1 | MODBUS_BAUD_RATE | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0->19200 1->9600

## T3_32I
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 1 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version High
5 | 1 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version Low
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
9 | 1 | MODBUS_PIC | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIC rev
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Baudrate Setting: 0 = 9600bps,1 = 19200bps
100 | 1 | T332I_INPUT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT1
101 | 1 | T332I_INPUT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT2
102 | 1 | T332I_INPUT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT3
103 | 1 | T332I_INPUT4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT4
104 | 1 | T332I_INPUT5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT5
105 | 1 | T332I_INPUT6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT6
106 | 1 | T332I_INPUT7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT7
107 | 1 | T332I_INPUT8 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT8
108 | 1 | T332I_INPUT9 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT9
109 | 1 | T332I_INPUT10 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT10
110 | 1 | T332I_INPUT11 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT11
111 | 1 | T332I_INPUT12 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT12
112 | 1 | T332I_INPUT13 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT13
113 | 1 | T332I_INPUT14 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT14
114 | 1 | T332I_INPUT15 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT15
115 | 1 | T332I_INPUT16 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT16
116 | 1 | T332I_INPUT17 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT17
117 | 1 | T332I_INPUT18 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT18
118 | 1 | T332I_INPUT19 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT19
119 | 1 | T332I_INPUT20 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT20
120 | 1 | T332I_INPUT21 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT21
121 | 1 | T332I_INPUT22 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT22
122 | 1 | T332I_INPUT23 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT23
123 | 1 | T332I_INPUT24 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT24
124 | 1 | T332I_INPUT25 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT25
125 | 1 | T332I_INPUT26 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT26
126 | 1 | T332I_INPUT27 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT27
127 | 1 | T332I_INPUT28 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT28
128 | 1 | T332I_INPUT29 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT29
129 | 1 | T332I_INPUT30 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT30
130 | 1 | T332I_INPUT31 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT31
131 | 1 | T332I_INPUT32 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | INPUT32
228 | 1 | T332I_RANGE1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0 = raw data,1 = 10K Celsius,2 = 10K Fahrenheit,3 = 0-100%,4 = ON/OFF,5 = OFF/ON,8 = typeIII 10K Celsius,9=TYPE iii 10K Fahrenheit,10 = No use, 11 =V0_5,12= V0_10,13 = I0_20ma.
229 | 1 | T332I_RANGE2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
230 | 1 | T332I_RANGE3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
231 | 1 | T332I_RANGE4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
232 | 1 | T332I_RANGE5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
233 | 1 | T332I_RANGE6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
234 | 1 | T332I_RANGE7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
235 | 1 | T332I_RANGE8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
236 | 1 | T332I_RANGE9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
237 | 1 | T332I_RANGE10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
238 | 1 | T332I_RANGE11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
239 | 1 | T332I_RANGE12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
240 | 1 | T332I_RANGE13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
241 | 1 | T332I_RANGE14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
242 | 1 | T332I_RANGE15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
243 | 1 | T332I_RANGE16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
244 | 1 | T332I_RANGE17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
245 | 1 | T332I_RANGE18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
246 | 1 | T332I_RANGE19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
247 | 1 | T332I_RANGE20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
248 | 1 | T332I_RANGE21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
249 | 1 | T332I_RANGE22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
250 | 1 | T332I_RANGE23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
251 | 1 | T332I_RANGE24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
252 | 1 | T332I_RANGE25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
253 | 1 | T332I_RANGE26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
254 | 1 | T332I_RANGE27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
255 | 1 | T332I_RANGE28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
256 | 1 | T332I_RANGE29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
257 | 1 | T332I_RANGE30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
258 | 1 | T332I_RANGE31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
259 | 1 | T332I_RANGE32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
260 | 1 | T332I_FILTER1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
261 | 1 | T332I_FILTER2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
262 | 1 | T332I_FILTER3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
263 | 1 | T332I_FILTER4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
264 | 1 | T332I_FILTER5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
265 | 1 | T332I_FILTER6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
266 | 1 | T332I_FILTER7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
267 | 1 | T332I_FILTER8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
268 | 1 | T332I_FILTER9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
269 | 1 | T332I_FILTER10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
270 | 1 | T332I_FILTER11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
271 | 1 | T332I_FILTER12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
272 | 1 | T332I_FILTER13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
273 | 1 | T332I_FILTER14 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
274 | 1 | T332I_FILTER15 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
275 | 1 | T332I_FILTER16 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
276 | 1 | T332I_FILTER17 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
277 | 1 | T332I_FILTER18 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
278 | 1 | T332I_FILTER19 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
279 | 1 | T332I_FILTER20 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
280 | 1 | T332I_FILTER21 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
281 | 1 | T332I_FILTER22 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
282 | 1 | T332I_FILTER23 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
283 | 1 | T332I_FILTER24 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
284 | 1 | T332I_FILTER25 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
285 | 1 | T332I_FILTER26 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
286 | 1 | T332I_FILTER27 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
287 | 1 | T332I_FILTER28 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
288 | 1 | T332I_FILTER29 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
289 | 1 | T332I_FILTER30 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
230 | 1 | T332I_FILTER31 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
231 | 1 | T332I_FILTER32 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer

## T3_8AI13O
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description
0 | 4 | MODBUS_SERIALNUMBER | 03 Read Holding Registers (4x) | 32 Bit Unsigned Integer LO_HI | serial numbler
4 | 1 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version High
5 | 1 | MODBUS_FIRMWARE_VERSION | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | firmware Version Low
6 | 1 | MODBUS_ADDRESS | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Modbus device address
7 | 1 | MODBUS_PRODUCT_MODEL | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Prodouct model
8 | 1 | MODBUS_HARDWARE_REV | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Hardware Version Number
9 | 1 | MODBUS_PIC | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | PIC rev
15 | 1 | MODBUS_BAUDRATE | 03_06 Read Holding and Write Single | 8 Bit Unsigned Integer | Baudrate Setting: 0 = 9600bps,1 = 19200bps
19 | 1 | MODBUS_RESPONSE_DELAY | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | MODBUS RESPONSE DELAY DEFAULT 0 = 2.5MS 1 = 7.5MS
100 | 1 | MODBUS_OUTPUT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
101 | 1 | MODBUS_OUTPUT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
102 | 1 | MODBUS_OUTPUT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
103 | 1 | MODBUS_OUTPUT4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
104 | 1 | MODBUS_OUTPUT5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
105 | 1 | MODBUS_OUTPUT6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
106 | 1 | MODBUS_OUTPUT7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
107 | 1 | MODBUS_OUTPUT8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
108 | 1 | MODBUS_OUTPUT9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
109 | 1 | MODBUS_OUTPUT10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
110 | 1 | MODBUS_OUTPUT11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
111 | 1 | MODBUS_OUTPUT12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
112 | 1 | MODBUS_OUTPUT13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
116 | 1 | MODBUS_SWITCH1_STATUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
117 | 1 | MODBUS_SWITCH2_STATUS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
118 | 2 | MODBUS_VALUE__INPUT1 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer LO_HI | Input1: 2 registers, Value = Reg118 * 65535 + Reg 119
120 | 2 | MODBUS_VALUE__INPUT2 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer LO_HI | Input2: 2 registers, Value = Reg120 * 65535 + Reg 121
122 | 2 | MODBUS_VALUE__INPUT3 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer LO_HI | Input3: 2 registers, Value = Reg122 * 65535 + Reg 123
124 | 2 | MODBUS_VALUE__INPUT4 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer LO_HI | Input4: 2 registers, Value = Reg124 * 65535 + Reg 125
126 | 2 | MODBUS_VALUE__INPUT5 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer LO_HI | Input5: 2 registers, Value = Reg126 * 65535 + Reg 127
128 | 2 | MODBUS_VALUE__INPUT6 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer LO_HI | Input6: 2 registers, Value = Reg128 * 65535 + Reg 129
130 | 2 | MODBUS_VALUE__INPUT7 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer LO_HI | Input7: 2 registers, Value = Reg130 * 65535 + Reg 131
132 | 2 | MODBUS_VALUE__INPUT8 | 03_06 Read Holding and Write Single | 32 Bit Unsigned Integer LO_HI | Input8: 2 registers, Value = Reg132 * 65535 + Reg 133
175 | 1 | MODBUS_ORIGINAL_AD_INPUT1 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Original AD data for input1
176 | 1 | MODBUS_ORIGINAL_AD_INPUT2 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Original AD data for input2
177 | 1 | MODBUS_ORIGINAL_AD_INPUT3 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Original AD data for input3
178 | 1 | MODBUS_ORIGINAL_AD_INPUT4 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Original AD data for input4
179 | 1 | MODBUS_ORIGINAL_AD_INPUT5 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Original AD data for input5
180 | 1 | MODBUS_ORIGINAL_AD_INPUT6 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Original AD data for input6
181 | 1 | MODBUS_ORIGINAL_AD_INPUT7 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Original AD data for input7
182 | 1 | MODBUS_ORIGINAL_AD_INPUT8 | 03 Read Holding Registers (4x) | 16 Bit Unsigned Integer | Original AD data for input8
183 | 1 | MODBUS_RANGE_INPUT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Range Setting for each input. 183 correspond to input1, 184 correspond to input2, etc. 0 = raw data, 1 = 10K Celsius, 2 = 10K Fahrenheit, 3 = 0-100% 4 = ON/OFF, 5 = OFF/ON 6 = Pulse Input 7 = Lighting Control 8 = type3 10K Celsius, 9=TYPE 3 10K Fahrenheit,10 = No use, 11 =V0_5,12= V0_10,13 = I0_20ma.
184 | 1 | MODBUS_RANGE_INPUT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
185 | 1 | MODBUS_RANGE_INPUT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
186 | 1 | MODBUS_RANGE_INPUT4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
187 | 1 | MODBUS_RANGE_INPUT5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
188 | 1 | MODBUS_RANGE_INPUT6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
189 | 1 | MODBUS_RANGE_INPUT7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
190 | 1 | MODBUS_RANGE_INPUT8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
191 | 1 | MODBUS_FILTER_INPUT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Input Filter Use these registers to smooth out the input readings 0 means fast, no filtering, 255 means slow, noise will be smoothed Default is 20
192 | 1 | MODBUS_FILTER_INPUT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
193 | 1 | MODBUS_FILTER_INPUT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
194 | 1 | MODBUS_FILTER_INPUT4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
195 | 1 | MODBUS_FILTER_INPUT5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
196 | 1 | MODBUS_FILTER_INPUT6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
197 | 1 | MODBUS_FILTER_INPUT7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
198 | 1 | MODBUS_FILTER_INPUT8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
199 | 1 | MODBUS_LIGHTING_ZONE_TIME_FOR_OUTPUT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lighting Feature How many minutes to toggle on zone1 lights for Units are in minutes Default is 60 Each 'Zone' is one output, time1 is associated with output1 and so on
200 | 1 | MODBUS_LIGHTING_ZONE_TIME_FOR_OUTPUT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
201 | 1 | MODBUS_LIGHTING_ZONE_TIME_FOR_OUTPUT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
202 | 1 | MODBUS_LIGHTING_ZONE_TIME_FOR_OUTPUT4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
203 | 1 | MODBUS_LIGHTING_ZONE_TIME_FOR_OUTPUT5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
204 | 1 | MODBUS_LIGHTING_ZONE_TIME_FOR_OUTPUT6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
205 | 1 | MODBUS_LIGHTING_ZONE_TIME_FOR_OUTPUT7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
206 | 1 | MODBUS_LIGHTING_ZONE_TIME_FOR_OUTPUT8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
207 | 1 | MODBUS_TIME_LEFT_FOR_OUTPUT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lighting Feature Time left for each lighting override event Shows how much time is left after a zone has been triggered on One time left timer for each 'zone' REG 207 = Output1 REG 208 = Output2 and so on
208 | 1 | MODBUS_TIME_LEFT_FOR_OUTPUT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
209 | 1 | MODBUS_TIME_LEFT_FOR_OUTPUT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
210 | 1 | MODBUS_TIME_LEFT_FOR_OUTPUT4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
211 | 1 | MODBUS_TIME_LEFT_FOR_OUTPUT5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
212 | 1 | MODBUS_TIME_LEFT_FOR_OUTPUT6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
213 | 1 | MODBUS_TIME_LEFT_FOR_OUTPUT7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
214 | 1 | MODBUS_TIME_LEFT_FOR_OUTPUT8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
215 | 1 | MODBUS_AUTO_MANUAL_ALL_OUTPUTS | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | 0= auto, 1=manual
216 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT1 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Lighting Features Use these registers to associate a particular output (zone of lighting) with a particular input (light switch) 0 means null, lighting features are disabled 1 means a particular output will toggle when a hit on input1 is detected 2 means a particular output will toggle when a hit on input2 is detected
217 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT2 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer | Example: set register 221 (Output6) to 8 means output6 will toggle on/off when input 8 is hit
218 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT3 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
219 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT4 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
220 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT5 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
221 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT6 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
222 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT7 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
223 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT8 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
224 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT9 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
225 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT10 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
226 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT11 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
227 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT12 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer
228 | 1 | MODBUS_LIGHT_SWITCH_FOR_OUT13 | 03_06 Read Holding and Write Single | 16 Bit Unsigned Integer

## Sample
Register_Address | Register_Length | Register_Name | Operation | Data_Format | Description

## FrontPage
1 | Add a search bar
2 | Show photos for each manuf up top
3 | Filter out devices
4 | Once you select a manufacturer you can see some details about them and a grid with all their device
| Photo | Title | Description
|  | T3 Controller | Some text about this item
|  | T3E Expansion IO | More text
|  | Co2 | Some text here too about this item
Humidity
|  | Air Lab | Some text here too about this item

## RevisionNote
version | Modify Table
Rev44 | CO2 | 已转MDB
REV45 | HUM,CO2 | 已转MDB
REV46 | T3BB | 已转MDB
REV47 | T3BB ,AFS | 已转MDB
REV48 | Tranducer2,T322I,T38I8O6DO,T3PT12 | 已转MDB
REV49 | AIRLAB_ESP
REV50 | HUM | 已转MDB
REV51 | T3BB | 已转MDB
REV52 | HUM | 已转MDB
REV53 | Transducer2 | 已转MDB
REV54 | PM2_5,T3BB | 已转MDB
REV55 | AFS | 已转MDB
REV58 | T3-32AI(ARM) | 已转MDB
REV61 | T3BB,T3-XB-ESP | 已转MDB
REV62 | T3BB,T3-XB-ESP,HUM
REV63 | T38I8O6DO,T322I,T3_32I_ARM,AFS,SPM1